## Sheet1
|  | 2017/18 Summer Peak |  |  | 2017 Winter Peak |  |  | 2018/19 Available Feeder Transfers | Total Nameplate Capacity | Normal Rating | Firm Delivery Capacity | Reverse N Rating^ | 10% POE FORECAST (MVA) | [5 empty] | System Limitation? | Hours>95% of Peak Load | Known Embedded Generation (MW)
Substation | SCADA SITE | MVA | MW | Date | MVA | MW | Date | MVA | MVA | MVA | MVA | (MVA) | Power Factor | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | (Y/N) | Hrs | PV Inverter System | Rotating
^ Reverse power limit of the transformers. Other system limitations may apply for embedded generation connections.
ADELAIDE CBD AREA
ADELAIDE CENTRAL REGION 66kV |  | 185.9756 | 180.8657 | 2018-01-19 |  |  |  |  | 525 | 525 | 270 | 525 | 0.96 | 211.875 | 212.2917 | 212.7083 | 213.125 | 213.5417 |  |  | 3.7718
East Terrace 11kV | Y | 38.5274 | 36.4039 | 2018-01-19 | 26.092 | 25.044 | 2017-06-05 | - | 63 | 62.2394 | 52.38 | 62.0667 | 0.94488 | 44.0913 | 44.7437 | 45.5831 | 45.8239 | 46.0566 | N | 13 | 1.4795 | -
Coromandel Place 11kV | Y | 46.133 | 44.5079 | 2018-01-19 | 31.123 | 30.518 | 2017-07-05 | - | 75 | 93 | 73.3333 | 75 | 0.96477 | 52.2559 | 55.2381 | 56.3306 | 56.6265 | 56.9103 | N | 13 | 0.25005 | -
Hindley Street 11kV | Y | 41.8638 | 41.7657 | 2018-01-19 | 26.867 | 26.098 | 2017-08-28 | - | 63 | 77.124 | 53.8 | 29.6351 | 0.99766 | 45.0029 | 45.746 | 46.6469 | 46.9308 | 47.2052 | N | 13 | 0.46457 | -
Whitmore Square 11kV | Y | 39.5218 | 37.7743 | 2018-01-19 | 24.742 | 24.192 | 2017-08-21 | - | 63 | 72.4102 | 51.5921 | 63 | 0.95578 | 42.5371 | 43.0432 | 43.6337 | 43.8812 | 44.1212 | N | 13 | 1.5279 | -
East Terrace 33kV | Y | 8.1957 | 7.9557 | 2017-11-29 | 7.44 | 6.257 | 2017-06-06 | - | 25 | 23.8 | 0 | 25 | 0.97072 | 9.4235 | 8.5419 | 8.7224 | 8.7959 | 8.8676 | N | 13 | 0 | -
Hindley Street 33kV | Y | 8.2498 | 7.7224 | 2018-01-19 | 5.969 | 5.357 | 2017-06-09 | - | 25 | 27.4 | 0 | 25 | 0.93607 | 9.7541 | 8.8248 | 8.9988 | 9.0618 | 9.1231 | N | 13 | 0.04988 | -
EASTERN SUBURBS
METRO EAST REGION 66kV |  | 675.577 | 655.8149 | 2018-01-19 |  |  |  |  | 1650 | 1650 | 1395 | 1650 | 0.97075 | 757.8261 | 761.5514 | 765.9944 | 768.4295 | 770.6477 |  |  | 174.4934
Burnside 11kV | Y | 12.4644 | 12.12 | 2018-01-28 | 9.88 | 9.75 | 2017-08-28 | 10.1716 | 25 | 31.2 | 0 | 25 | 0.97237 | 13.2894 | 13.1504 | 13.1454 | 13.1115 | 13.0795 | N | 6 | 4.4192 | -
Campbelltown 11kV | Y | 45.5517 | 44.0568 | 2018-01-19 | 28.17 | 27.796 | 2017-08-28 | 14.2097 | 64 | 73.6 | 38.1 | 64 | 0.96718 | 52.468 | 52.8632 | 53.3121 | 53.7027 | 54.0449 | N | 7 | 15.0243 | -
Clearview 11kV | Y | 21.6001 | 21.2589 | 2018-02-07 | 15.487 | 15.41 | 2017-07-07 | 19.87 | 20 | 26.5973 | 15 | 18.6647 | 0.98421 | 22.4836 | 22.5281 | 22.4415 | 22.5592 | 22.6715 | N | 7 | 8.4281 | -
Golden Grove 11kV | Y | 44.4229 | 43.0453 | 2018-02-07 | 33.071 | 32.665 | 2017-08-28 | 12.0435 | 75 | 84.6321 | 59.6409 | 30.2444 | 0.96899 | 48.5731 | 48.6017 | 48.552 | 48.6148 | 48.6687 | N | 6 | 19.4009 | -
Harrow 11kV | Y | 18.0924 | 17.3782 | 2018-01-19 | 16.874 | 16.64 | 2017-08-04 | 14.3033 | 20 | 28.3147 | 15 | 19.87 | 0.96052 | 20.5706 | 20.6743 | 20.8057 | 20.9694 | 21.1304 | N | 6 | 6.0306 | -
Hillcrest 11kV | Y | 33.3275 | 32.44 | 2018-02-07 | 32.421 | 32.07 | 2017-08-04 | 21.5188 | 50 | 61.6816 | 36.8 | 49.9042 | 0.97337 | 38.2815 | 38.2801 | 38.3352 | 38.4333 | 38.5273 | N | 7 | 10.5006 | -
Holden Hill 11kV | Y | 35.0825 | 34.3867 | 2017-11-21 | 27.817 | 27.498 | 2017-08-28 | 24.4547 | 42 | 46.713 | 25 | 41.3913 | 0.98017 | 38.1792 | 38.3867 | 38.5387 | 38.7255 | 38.9057 | N | 7 | 11.2055 | -
Hope Valley 11kV | Y | 16.5442 | 16.01 | 2018-02-07 | 16.026 | 15.77 | 2017-08-03 | 13.5283 | 25 | 31.2 | 0 | 25 | 0.96977 | 19.0083 | 18.9836 | 18.9717 | 19.0213 | 19.0637 | N | 5 | 7.8915 | 3.86
Ingle Farm 11kV | Y | 33.754 | 32.7827 | 2018-02-07 | 23.913 | 23.667 | 2017-08-28 | 17.526 | 45 | 51.7129 | 26 | 23.7383 | 0.97122 | 37.2319 | 37.2853 | 37.2847 | 37.459 | 37.6294 | N | 7 | 12.9851 | -
Kent Town 11kV | Y | 30.5155 | 28.82 | 2018-02-08 | 19.9449 | 19.2 | 2017-06-08 | 17.842 | 50 | 59.1822 | 29.8 | 50 | 0.94444 | 33.5968 | 33.6866 | 33.8302 | 33.8471 | 33.8584 | N | 9 | 4.35 | -
Kilburn South 11kV | Y | 14.1213 | 13.66 | 2018-01-18 | 10.897 | 10.79 | 2017-07-06 | 14.554 | 32 | 36.195 | 0 | 32 | 0.96733 | 14.9312 | 14.8321 | 14.8005 | 14.7857 | 14.7715 | N | 7 | 3.0882 | -
Linden Park 11kV | Y | 37.7626 | 36.2662 | 2018-01-19 | 27.332 | 26.72 | 2017-08-28 | 19.2785 | 50 | 55.6587 | 30.48 | 20.6354 | 0.96037 | 41.3709 | 41.236 | 41.225 | 41.1665 | 41.0678 | N | 7 | 11.1111 | -
North Adelaide 11kV | Y | 20.1862 | 19.58 | 2018-01-19 | 15.912 | 11.09 | 2017-08-30 | 8.0187 | 64 | 72.104 | 38.1 | 64 | 0.96997 | 22.5643 | 22.5845 | 22.6687 | 22.7004 | 22.7306 | N | 13 | 3.4393 | -
Northfield 11kV | Y | 19.3029 | 18.3225 | 2018-02-07 | 14.345 | 13.999 | 2017-06-29 | 18.3768 | 20 | 26.5321 | 15 | 18.619 | 0.96997 | 20.5402 | 20.7098 | 20.9034 | 21.0923 | 21.2777 | N | 7 | 7.8656 | -
Norwood 11kV | Y | 52.5997 | 52.5073 | 2018-02-08 | 39.789 | 38.992 | 2017-08-28 | 22.1387 | 63 | 73.7958 | 51.4185 | 63 | 0.99824 | 57.9704 | 57.933 | 57.7657 | 57.6596 | 57.5415 | N | 7 | 15.6052 | -
Prospect 11kV | Y | 29.7716 | 27.9412 | 2017-11-29 | 20.18 | 19.542 | 2017-06-23 | 28.3635 | 42 | 49.4207 | 26.2 | 41.8482 | 0.93852 | 30.2708 | 30.135 | 30.155 | 30.1296 | 30.1037 | N | 9 | 7.2908 | 4.4
Tea Tree Gully 11kV | Y | 30.8851 | 30.072 | 2018-01-18 | 23.948 | 23.744 | 2017-08-16 | 13.2996 | 42 | 49.0682 | 26.4 | 19.667 | 0.97367 | 33.3328 | 33.3203 | 33.2499 | 33.3225 | 33.3654 | N | 6 | 12.4726 | -
Woodforde 11kV | Y | 37.1205 | 35.626 | 2018-02-07 | 26.131 | 25.618 | 2017-08-28 | 20.8825 | 42 | 50.476 | 27 | 41.8971 | 0.95974 | 41.8847 | 42.0029 | 42.0365 | 42.1559 | 42.2665 | N | 6 | 13.3848 | -
WESTERN SUBURBS
METRO WEST REGION 66kV | Y | 398.4598 | 396.4562 | 2018-01-18 |  |  |  |  | 885 | 885 | 660 | 885 | 0.99497 | 434.4535 | 438.8784 | 448.0867 | 449.6526 | 451.3407 |  |  | 104.5764
Athol Park 11kV | Y | 17.6867 | 16.3874 | 2018-02-09 | 15.159 | 14.14 | 2017-06-21 | 18.5872 | 20 | 26.5066 | 14.3 | 18.6011 | 0.92654 | 18.1269 | 17.8693 | 19.9799 | 19.8573 | 19.743 | N | 7 | 6.036 | -
Blackpool 11kV | Y | 11.7147 | 11.3717 | 2018-01-18 | 10.022 | 9.913 | 2017-08-06 | 5.1313 | 16 | 19.9351 | 10.53 | 11.1598 | 0.97072 | 15.7478 | 15.7964 | 15.7383 | 15.8381 | 15.942 | N | 7 | 5.7642 | -
Cavan 11kV | Y | 39.9328 | 36.98 | 2018-01-19 | 23.926 | 22.87 | 2017-07-20 | 20.8326 | 50 | 58.2264 | 31.6 | 49.1777 | 0.92606 | 41.4524 | 41.6877 | 42.2523 | 42.3409 | 42.4446 | N | 7 | 4.9324 | -
Cheltenham 11kV | Y | 11.1989 | 11.05 | 2018-01-18 | 8.628 | 8.59 | 2017-07-20 | 8.1697 | 25 | 29.9 | 0 | 25 | 0.98671 | 10.4785 | 10.5953 | 12.7175 | 12.8171 | 12.9211 | N | 9 | 3.3449 | -
Cheltenham 33kV | Y | 3.5356 | 3.1255 | 2017-12-14 | 6.027 | 4.82 | 2017-08-15 | 4.1343 | 20 | 19 | 0 | 20 | 0.88402 | 4.5146 | 4.5318 | 0 | 0 | 0 | N | 5 | 0.1 | -
Croydon 11kV | Y | 31.7848 | 31.5174 | 2017-11-29 | 17.123 | 16.446 | 2017-06-08 | 24.1236 | 42 | 48.4 | 25.6 | 42 | 0.99159 | 24.7649 | 24.8864 | 24.9303 | 25.1293 | 25.338 | N | 9 | 5.5758 | -
Croydon Park 11kV | Y | 15.6651 | 15.0628 | 2018-02-08 | 11.238 | 11.104 | 2017-07-03 | 17.0124 | 20 | 26.4221 | 13.685 | 11.5932 | 0.96155 | 17.0935 | 16.9592 | 16.823 | 16.8002 | 16.7845 | N | 7 | 4.7266 | -
Findon 11kV | Y | 16.8491 | 16.2923 | 2018-01-18 | 15.929 | 15.656 | 2017-07-10 | 18.1136 | 20 | 24.8215 | 14.1 | 17.4186 | 0.96696 | 18.9053 | 19.1291 | 19.208 | 19.384 | 19.5633 | N | 6 | 3.9347 | -
Flinders Park 11kV | Y | 22.4272 | 21.6164 | 2018-01-18 | 12.473 | 12.264 | 2017-08-28 | 19.8756 | 20 | 27.2609 | 14.1 | 19.2508 | 0.96385 | 21.8168 | 22.2182 | 22.44 | 22.7831 | 23.13 | N | 6 | 5.1562 | -
Fulham Gardens 11kV | Y | 38.7658 | 37.2599 | 2018-01-18 | 27.248 | 26.69 | 2017-08-04 | 18.7986 | 42 | 48.9986 | 24.8 | 21.059 | 0.96115 | 43.6278 | 43.9382 | 43.9095 | 44.1869 | 44.4725 | N | 7 | 12.7268 | -
Glanville 7.6kV | Y | 8.4411 | 8.287 | 2018-01-18 | 6.377 | 6.312 | 2017-08-04 | 11.3976 | 16 | 20.3597 | 12 | 14.2875 | 0.98174 | 8.5957 | 8.4152 | 8.1336 | 8.0673 | 8.0037 | N | 6 | 4.4817 | -
Henley South 11kV | Y | 33.4839 | 32.3839 | 2018-01-18 | 23.74 | 23.316 | 2017-07-03 | 16.5685 | 48 | 55.7251 | 30.48 | 23.9097 | 0.96715 | 35.6842 | 36.0107 | 36.1002 | 36.34 | 36.5884 | N | 7 | 9.9071 | -
Kilburn 11kV | Y | 48.7675 | 44.7762 | 2018-03-06 | 45.06 | 41.3579 | 2017-06-21 | 26.3581 | 63 | 76.1707 | 54.3481 | 36.4226 | 0.91816 | 45.3146 | 45.9516 | 46.477 | 46.615 | 46.7594 | N | 3 | 3.2874 | 2
Kilkenny 11kV | Y | 20.6298 | 20.132 | 2018-01-19 | 17.809 | 17.416 | 2017-06-08 | 13.3952 | 50 | 55.9052 | 31.4 | 48.5288 | 0.97587 | 20.8405 | 20.8153 | 20.8037 | 20.7007 | 20.6038 | N | 9 | 3.6591 | -
Largs North 7.6kV | Y | 14.6035 | 14.1204 | 2018-01-18 | 10.795 | 10.636 | 2017-08-06 | 6.7914 | 20 | 27.4987 | 15 | 19.9266 | 0.96692 | 16.1227 | 16.2529 | 16.2684 | 16.3483 | 16.4309 | N | 9 | 5.7308 | -
Lefevre 11kV | Y | 11.1484 | 10.63 | 2017-12-13 | 9.563 | 9.28 | 2017-07-06 | 2.5953 | 64 | 72.1769 | 38.1 | 64 | 0.9535 | 7.2306 | 7.3242 | 7.4038 | 7.4077 | 7.4125 | N | 4 | 0.154 | -
New Richmond 11kV | Y | 31.6508 | 30.0262 | 2018-01-19 | 20.476 | 20.077 | 2017-07-03 | 18.1903 | 42 | 51.1293 | 26.4 | 42 | 0.94867 | 31.1535 | 31.1795 | 31.1584 | 31.2515 | 31.3559 | N | 7 | 7.1363 | -
New Osborne 11kV | Y | - | - | - | - | - | - | 8 | 10 | 9.5 | 0 | - | 0 | - | - | - | - | - | - | - | - | -
Port Adelaide 11kV | Y | 7.3373 | 6.7093 | 2018-01-19 | 5.919 | 5.56 | 2017-06-08 | 5.011 | 16 | 19.9093 | 10.53 | 16 | 0.91441 | 10.674 | 10.5918 | 10.5126 | 10.5037 | 10.4993 | N | 7 | 2.6962 | -
Port Adelaide North 11kV | Y | 23.0702 | 21.1797 | 2018-02-05 | 22.53 | 21.15 | 2017-06-30 | 13.2149 | 42 | 47.1921 | 25.3 | 19.4667 | 0.91806 | 20.1883 | 20.3102 | 20.3693 | 20.3708 | 20.3761 | N | 9 | 2.4953 | 2
Queenstown 7.6kV | Y | 12.225 | 11.7425 | 2018-01-18 | 10.435 | 10.177 | 2017-07-03 | 2.8695 | 16 | 22.7006 | 12 | 15.9303 | 0.96053 | 11.8445 | 15.4595 | 15.4056 | 15.4633 | 15.5274 | N | 9 | 4.8838 | -
Thebarton 11kV | Y | 19.8267 | 18.4692 | 2018-02-09 | 21.714 | 20.914 | 2017-06-08 | 19.4564 | 42 | 49 | 25.8 | 42 | 0.93153 | 27.9911 | 27.9656 | 27.8933 | 27.8408 | 27.7962 | N | 7 | 5.0415 | -
Woodville 11kV | Y | 10.7368 | 9.9852 | 2017-11-20 | 3.558 | 3.45 | 2017-08-21 | 9.2381 | 25 | 28.2 | 0 | 25 | 0.93 | 10.8765 | 7.1216 | 7.9138 | 7.9703 | 8.0304 | N | - | 1.936 | -
Woodville 33kV | Y | 1.1117 | 1.007 | 2018-02-07 | 4.6798 | 4.1578 | 2017-06-15 | 0.33157 | 40 | 37.89 | 20 | 37.89 | 0.90578 | 1.048 | 1.0015 | 0 | 0 | 0 | N | 9 | 0 | -
NORTHERN SUBURBS
METRO NORTH REGION 66kV | Y | 298.0916 | 296.003 | 2018-02-08 |  |  |  |  | 870 | 870 | 693 | 870 | 0.99299 | 322.9455 | 323.3163 | 325.1649 | 326.6408 | 328.2495 |  |  | 105.2941
Angle Vale 11kV | Y | 17.4325 | 16.513 | 2018-02-07 | 11.334 | 10.96 | 2017-06-07 | 12.8052 | 22.5 | 27.3493 | 20.4785 | 22.0559 | 0.94726 | 19.1531 | 19.4703 | 19.858 | 20.1488 | 20.447 | N | 5 | 8.6327 | -
Direk 11kV | Y | 21.2057 | 20.48 | 2018-02-07 | 17.763 | 17.32 | 2017-06-20 | 20.8604 | 50 | 56.4 | 29.8 | 50 | 0.96578 | 22.5573 | 22.3238 | 22.3148 | 22.1895 | 22.0753 | N | 9 | 6.2564 | -
Edinburgh 11kV | Y | 14.5595 | 13.881 | 2018-02-07 | 13.649 | 13.1 | 2017-07-31 | 7.4559 | 50 | 57.058 | 32 | 49.5295 | 0.9534 | 15.5432 | 15.4822 | 15.4475 | 15.4624 | 15.4827 | N | 9 | 2.1492 | -
Elizabeth Downs 11kV | Y | 41.5963 | 40.5593 | 2018-02-08 | 27.323 | 27.164 | 2017-08-03 | 15.4079 | 50 | 59.6 | 31.9 | 50 | 0.97507 | 45.732 | 46.1111 | 46.5693 | 47.0018 | 47.4509 | N | 5 | 14.1261 | -
Elizabeth Heights 11kV | Y | 17.8271 | 17.3572 | 2018-01-19 | 16.172 | 16.073 | 2017-06-26 | 12.7127 | 20 | 27.5654 | 15 | 19.3441 | 0.97364 | 20.143 | 19.9513 | 19.8204 | 19.7804 | 19.7482 | N | 6 | 7.1971 | -
Elizabeth South 11kV | Y | 9.9033 | 9.6392 | 2018-02-07 | 17.088 | 16.839 | 2017-06-08 | 10.662 | 20 | 28.4301 | 15 | 20 | 0.97333 | 10.8447 | 10.7802 | 10.7196 | 10.7087 | 10.7011 | N | 5 | 2.098 | -
Evanston 11kV | Y | 35.6295 | 35.0321 | 2018-02-08 | 25.161 | 24.905 | 2017-08-28 | 9.6588 | 50 | 57.6602 | 30.48 | 49.7826 | 0.98323 | 40.1248 | 40.514 | 41.0532 | 41.4322 | 41.821 | N | 6 | 16.0171 | 2.2
Parafield Gardens 11kV | Y | 26.4971 | 25.92 | 2018-02-07 | 17.447 | 17.36 | 2017-08-04 | 7.9024 | 64 | 70.2 | 38.1 | 64 | 0.97822 | 29.2797 | 29.3899 | 29.5379 | 29.7864 | 30.0468 | N | 5 | 12.6531 | -
Paralowie 11kV | Y | 17.3823 | 17.3175 | 2018-02-07 | 12.235 | 12.117 | 2017-08-28 | 6.403 | 20 | 27.4831 | 14.2 | 19.3774 | 0.99627 | 18.8975 | 18.9698 | 19.0581 | 19.1002 | 19.1461 | N | 5 | 5.5056 | -
Penfield 11kV | Y | 22.3833 | 21.1 | 2018-02-08 | 16.667 | 16.02 | 2017-06-08 | 15.4119 | 50 | 51.3624 | 28.3 | 49.8424 | 0.94267 | 24.8843 | 25.1679 | 25.5939 | 25.8429 | 26.1029 | N | 9 | 2.9135 | -
Salisbury 11kV | Y | 51.9307 | 51.7484 | 2018-02-08 | 37.401 | 37.356 | 2017-07-03 | 16.7756 | 63 | 72.5812 | 49.5018 | 31.1945 | 0.99649 | 56.8098 | 56.2204 | 56.1735 | 56.1432 | 56.145 | N | 7 | 17.4176 | -
Smithfield West 11kV | Y | 17.2148 | 17.08 | 2018-01-28 | 11.722 | 11.72 | 2017-08-06 | 12.6463 | 32 | 36.195 | 0 | 32 | 0.99217 | 18.8949 | 18.9687 | 19.1303 | 19.3465 | 19.5743 | N | 5 | 5.7128 | -
Virginia 11kV | Y | 6.4334 | 5.8391 | 2018-02-08 | 4.123 | 4 | 2017-06-01 | 3.5526 | 12.5 | 14.9 | 0 | 12.5 | 0.90762 | 6.6282 | 6.5663 | 6.5848 | 6.6242 | 6.6691 | N | 5 | 2.659 | -
Two Wells 11kV | Y | 3.0806 | 3.0341 | 2018-02-07 | 2.281 | 2.28 | 2017-08-28 | 4.0492 | 12.5 | 16.6 | 0 | 12.5 | 0.9849 | 3.3451 | 3.3578 | 3.3794 | 3.4122 | 3.4466 | N | 5 | 1.8898 | -
SOUTHERN SUBURBS
METRO SOUTH REGION 66kV | Y | 627.4528 | 624.1409 | 2018-01-18 |  |  |  |  | 1515 | 1527 | 1275 | 1515 | 0.99472 | 679.0922 | 681.3933 | 680.6778 | 682.2744 | 684.0019 |  |  | 245.0813
Ascot Park 11kV | Y | 16.4689 | 16.1748 | 2018-01-19 | 12.614 | 12.511 | 2017-08-04 | 17.3342 | 21 | 27.025 | 0 | 10.1 | 0.98214 | 17.9376 | 17.8557 | 17.5828 | 17.5801 | 17.5811 | N | 7 | 5.944 | -
Blackwood 11kV | Y | 25.9941 | 25.4094 | 2018-01-19 | 21.412 | 21.239 | 2017-08-28 | 14.5569 | 50 | 57.8756 | 30.48 | 19.7875 | 0.9775 | 28.7023 | 28.8975 | 28.9054 | 29.0403 | 29.1628 | N | 6 | 11.7842 | -
Clarence Gardens 11kV | Y | 16.8481 | 16.43 | 2018-01-19 | 17.668 | 17.55 | 2017-06-07 | 17.9518 | 32 | 35.9 | 0 | 32 | 0.97519 | 18.1296 | 17.9828 | 17.8263 | 17.765 | 17.7107 | N | 6 | 6.3008 | -
Cudmore Park 11kV | Y | 14.0225 | 12.9643 | 2018-02-08 | 14.843 | 14.215 | 2017-06-08 | 19.953 | 20 | 22.1309 | 12.96 | 19.9721 | 0.92453 | 17.0762 | 17.1177 | 17.1802 | 17.1607 | 17.1465 | N | 9 | 3.2692 | -
Glenelg North 11kV | Y | 19.9587 | 19.0808 | 2018-01-18 | 13.994 | 13.701 | 2017-08-04 | 10.4647 | 20 | 27.9125 | 15 | 19.5877 | 0.95602 | 21.9009 | 22.0242 | 21.9525 | 21.9878 | 22.0267 | N | 7 | 4.4089 | -
Happy Valley 11kV | Y | 31.0578 | 30.1521 | 2018-01-19 | 23.761 | 23.495 | 2017-07-03 | 7.9282 | 50 | 59.8 | 31.9 | 50 | 0.97084 | 32.5244 | 32.567 | 32.403 | 32.4145 | 32.3987 | N | 5 | 15.3646 | -
Keswick 11kV | Y | 34.2794 | 32.1109 | 2018-02-09 | 26.924 | 25.816 | 2017-08-21 | 24.5269 | 42 | 49.0691 | 25.8 | 42 | 0.93674 | 37.5677 | 37.6155 | 37.5713 | 37.338 | 37.1111 | N | 9 | 3.8596 | -
Kingswood 11kV | Y | 44.7682 | 42.6452 | 2018-01-19 | 33.592 | 32.822 | 2017-08-28 | 26.2541 | 64 | 71.2 | 37.5 | 64 | 0.95258 | 49.8141 | 50.1117 | 50.4185 | 50.5298 | 50.6554 | N | 6 | 12.8919 | -
Lower Mitcham 11kV | Y | 17.4481 | 16.9764 | 2018-01-19 | 15.203 | 15.019 | 2017-07-20 | 18.094 | 20 | 28.2171 | 15 | 19.8015 | 0.97297 | 19.2986 | 19.3333 | 19.2561 | 19.2534 | 19.2547 | N | 7 | 6.2171 | -
Morphettville 11kV | Y | 22.8527 | 21.4038 | 2018-01-18 | 17.858 | 17.311 | 2017-06-07 | 14.0062 | 20 | 27.9874 | 15 | 19.991 | 0.9366 | 24.1393 | 24.4261 | 24.4727 | 24.6672 | 24.8665 | N | 7 | 6.0069 | -
North Unley 11kV | Y | 16.7188 | 15.8367 | 2018-02-09 | 14.822 | 14.765 | 2017-07-20 | 17.3847 | 20 | 25.3934 | 13.5 | 19.5433 | 0.94724 | 19.1522 | 19.2236 | 19.2225 | 19.2329 | 19.2476 | N | 9 | 3.3443 | -
Oaklands 11kV | Y | 42.3879 | 42.0476 | 2018-01-18 | 29.819 | 29.211 | 2017-06-01 | 21.4213 | 48 | 57.4996 | 30.3 | 19.8243 | 0.99197 | 43.834 | 44.2885 | 44.4434 | 44.7189 | 45.0029 | N | 9 | 11.5088 | -
Panorama 11kV | Y | 22.8602 | 22.3 | 2018-01-19 | 18.425 | 18.23 | 2017-08-04 | 27.6777 | 50 | 58.2 | 30.7 | 50 | 0.97549 | 24.7683 | 24.7867 | 24.6795 | 24.6366 | 24.5986 | N | 7 | 8.0348 | -
Plympton 11kV | Y | 20.6313 | 19.8701 | 2018-01-18 | 17.476 | 16.938 | 2017-06-07 | 18.4421 | 20 | 28.4291 | 15 | 19.9502 | 0.96311 | 22.8697 | 22.8172 | 22.6143 | 22.5139 | 22.4176 | N | 7 | 5.0185 | -
Seacombe 11kV | Y | 39.7197 | 39.6291 | 2018-01-19 | 34.668 | 34.197 | 2017-08-04 | 18.5619 | 50 | 59.2 | 31.6 | 50 | 0.99772 | 44.7823 | 44.9561 | 44.9893 | 45.0662 | 45.1543 | N | 7 | 14.5011 | -
Sheidow Park 11kV | Y | 22.8309 | 22.7232 | 2018-01-18 | 19.873 | 19.749 | 2017-07-27 | 11.1972 | 25 | 35 | 18.6 | 11.2 | 0.99528 | 24.7683 | 25.0662 | 25.1709 | 25.4097 | 25.6529 | N | 5 | 11.706 | -
Tonsley Park 11kV | Y | 19.1277 | 18.5641 | 2018-02-09 | 13.779 | 13.488 | 2017-06-08 | 13.2108 | 30 | 40.0554 | 28.8686 | 29.5047 | 0.97054 | 22.4896 | 22.7807 | 23.0274 | 23.2013 | 23.3823 | N | 9 | 3.3649 | -
NOARLUNGA AREA | N
Aldinga 11kV | Y | 18.2658 | 17.8702 | 2018-01-18 | 14.511 | 14.426 | 2017-07-16 | 3.7612 | 25 | 33.2 | 17.7 | 25 | 0.97834 | 19.155 | 19.5413 | 19.7549 | 20.1052 | 20.4615 | N | 5 | 8.9413 | -
Clarendon 11kV | Y | 2.8162 | 2.7238 | 2018-01-18 | 1.564 | 1.485 | 2017-08-07 | 1.8416 | 2.5 | 3.25 | 0 | 1.9 | 0.96719 | 2.3974 | 2.4002 | 2.3822 | 2.3909 | 2.4 | N | 2 | 1.852 | -
Hackham 11kV | Y | 13.4419 | 13.19 | 2018-01-18 | 10.107 | 10.06 | 2017-08-04 | 12.7416 | 25 | 31.6 | 0 | 25 | 0.98126 | 13.794 | 13.6744 | 13.4643 | 13.4143 | 13.3681 | N | 5 | 7.1371 | -
McLaren Flat TF1 11kV | Y | 7.1447 | 6.5017 | 2018-02-09 | 4.92 | 4.52 | 2017-08-04 | 6.25 | 12.5 | 15.5 | 0 | 12.5 | 0.91 | 6.6629 | 6.5483 | 6.5381 | 6.514 | 6.4956 | N | 9 | 3.6315 | -
McLaren Flat TF2 11kV | Y | 2.2673 | 2.1733 | 2018-02-07 | 1.293 | 1.268 | 2017-07-03 | 1.94 | 12.5 | 15.2 | 0 | 12.5 | 0.95856 | 2.7794 | 2.8089 | 2.8329 | 2.8505 | 2.8689 | N | 9 | 0.95719 | -
Morphett Vale East 11kV | Y | 31.2451 | 30.7113 | 2018-01-18 | 23.151 | 23.086 | 2017-07-03 | 14.585 | 48 | 57.3425 | 30.48 | 48 | 0.98292 | 35.638 | 35.6591 | 35.3403 | 35.3318 | 35.3286 | N | 6 | 16.5694 | -
Noarlunga Centre 11kV | Y | 19.5753 | 18.4495 | 2018-01-19 | 12.121 | 11.789 | 2017-08-04 | 9.0817 | 20 | 28.2723 | 15 | 19.8402 | 0.94249 | 19.2711 | 19.3213 | 19.3533 | 19.3449 | 19.3417 | N | 9 | 3.2543 | -
Port Noarlunga 11kV | Y | 29.7118 | 29.31 | 2018-01-18 | 21.204 | 21.14 | 2017-08-04 | 20.6418 | 50 | 63.0903 | 37 | 49.7557 | 0.98648 | 30.5682 | 30.8604 | 30.9779 | 31.1621 | 31.3531 | N | 5 | 11.8144 | -
Port Stanvac 11kV | Y | 29.9293 | 29.9228 | 2018-01-18 | 26.557 | 26.373 | 2017-08-03 | 25.7415 | 50 | 59 | 31.1 | 50 | 0.99978 | 32.3778 | 31.9847 | 31.7167 | 31.5397 | 31.3784 | N | 9 | 11.3785 | 21
Seaford 11kV | Y | 8.6973 | 8.539 | 2018-01-18 | 7.507 | 7.485 | 2017-07-03 | 8.6659 | 12.5 | 15.8 | 0 | 12.5 | 0.9818 | 9.8178 | 10.0036 | 10.1341 | 10.3145 | 10.4975 | N | 7 | 4.8769 | -
Willunga 11kV | Y | 4.3052 | 4.0892 | 2018-01-18 | 3.303 | 3.2904 | 2017-08-04 | 5.48 | 5 | 6.7 | 0 | 5 | 0.94984 | 4.4459 | 4.4487 | 4.4224 | 4.4361 | 4.4511 | N | 5 | 2.8461 | -
McLaren Vale 11kV | Y | 2.4349 | 2.3619 | 2018-02-09 | 2.05 | 1.887 | 2017-06-30 | 2.5474 | 5 | 5.4 | 3 | 5 | 0.95856 | 2.6605 | 2.7061 | 2.7418 | 2.7873 | 2.834 | N | 7 | 1.345 | -
Willunga 33kV | Y | 2.7036 | 2.6012 | 2018-02-09 | 2.133 | 2.121 | 2017-06-30 | 0 | 7.5 | 10.6 | 0 | 7.5 | 0.96212 | 3.0601 | 3.0922 | 3.1256 | 3.1643 | 3.2046 | N | 5 | 1.4214 | -
McLaren Vale Vineyard 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.99472 | 0.049864 | 0.049884 | 0.049904 | 0.049924 | 0.049945 | N | 7 | 0 | -
FLEURIEU PENINSULA | N
Goolwa 11kV | Y | 12.4697 | 12.4577 | 2018-01-18 | 12.691 | 12.632 | 2017-06-10 | 0.4016 | 25 | 33.4 | 17.8 | 25 | 0.99904 | 15.6531 | 15.593 | 15.5525 | 15.7118 | 15.885 | N | 5 | 9.0574 | -
Square Water Hole 11kV | Y | 3.969 | 3.7301 | 2018-01-18 | 3.771 | 3.716 | 2017-07-08 | 3.597 | 5 | 7.125 | 0 | 5 | 0.93982 | 4.3009 | 4.2852 | 4.2548 | 4.2557 | 4.258 | N | 5 | 2.5034 | -
Victor Harbor 11kV | Y | 24.05 | 24 | 2018-01-18 | 19.893 | 19.78 | 2017-06-10 | 0 | 50 | 62.7333 | 36.9 | 49.6308 | 0.99792 | 24.8077 | 24.7274 | 24.6502 | 24.7164 | 24.798 | N | 5 | 14.6864 | -
Myponga 11kV | Y | 6.1828 | 5.8695 | 2018-01-18 | 4.726 | 4.604 | 2017-08-03 | 4.8492 | 10 | 14.102 | 7.5 | 9.8961 | 0.94932 | 5.9628 | 5.9922 | 5.9828 | 6.0032 | 6.025 | N | 5 | 2.477 | -
Yankalilla 11kV | Y | 6.8408 | 6.6121 | 2018-01-27 | 5.056 | 5.032 | 2017-06-10 | 8.03 | 12.5 | 16.6 | 0 | 12.5 | 0.96656 | 7.6779 | 7.7349 | 7.7157 | 7.7763 | 7.8325 | N | 5 | 3.5689 | -
Yankalilla 33kV | Y | 1.271 | 1.2634 | 2018-01-27 | 1.282 | 1.2795 | 2017-06-10 | 0 | 12.5 | 17.6 | 0 | 12.5 | 0.99404 | 0.99953 | 1.0007 | 1.004 | 1.0025 | 1.0014 | N | 5 | 0.62493 | -
Hay Flat 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.99472 | 0.049864 | 0.049884 | 0.049904 | 0.049924 | 0.049945 | N | 6 | 0.01019 | -
Yankalilla Hill 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.99472 | 0.019945 | 0.019954 | 0.019962 | 0.01997 | 0.019978 | N | 6 | 0 | -
Wirrina Cove 11kV | N | - | - | - | - | - | - | 0 | 1.5 | 1.95 | 0 | 1.5 | 0.99472 | 0.69809 | 0.69837 | 0.69866 | 0.69894 | 0.69922 | N | 6 | 0.0767 | -
Second Valley 11kV | N | - | - | - | - | - | - | 0.5643 | 0.5 | 0.65 | 0 | 0.5 | 0.99472 | 0.29918 | 0.2993 | 0.29942 | 0.29955 | 0.29967 | N | 6 | 0.38084 | -
Rapid Bay 11kV | N | - | - | - | - | - | - | 0 | 0.315 | 0.4095 | 0 | 0.315 | 0.99472 | 0.069809 | 0.069837 | 0.069866 | 0.069894 | 0.069922 | N | 6 | 0.029 | -
Salt Cliffs 11kV | N | - | - | - | - | - | - | 0.43991 | 0.5 | 0.65 | 0 | 0.5 | 0.99472 | 0.19945 | 0.19954 | 0.19962 | 0.1997 | 0.19978 | N | 6 | 0.1225 | -
Cape Jervis 33kV | Y | MVA: 40; MVA: 40; MVA: 0; (MVA): 40 | [9 empty] | 35
Cape Jervis 11kV | Y | 0.55888 | 0.51417 | 2018-01-27 | 0.48 | 0.441 | 2017-08-05 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.92 | 0.63073 | 0.64567 | 0.65952 | 0.67335 | 0.68716 | Y | 6 | 0.40582 | -
Penneshaw 11kV | Y | 0.7113 | 0.64994 | 2018-01-18 | 0.603 | 0.556 | 2017-08-02 | 0.75 | 1.5 | 1.95 | 0 | 1.5 | 0.91374 | 0.64371 | 0.64346 | 0.63152 | 0.63898 | 0.64664 | N | 7 | 0.33906 | -
AMERICAN RIVER REG 33kV | Y | 5.5463 | 5.352 | 2018-01-18 | 4.361 | 4.284 | 2017-06-28 | 0 | 10 | 12.5 | 0 | 10 | 0.96498 | 5.2175 | 5.3334 | 5.4411 | 5.4735 | 5.5065 | N | 5 | - | -
American River 11kV | Y | 0.42866 | 0.418 | 2018-01-18 | 0.348 | 0.345 | 2017-08-17 | 0 | 3 | 3.9 | 0 | 3 | 0.97513 | 0.40108 | 0.39045 | 0.37367 | 0.36708 | 0.36103 | N | 5 | 0.43087 | -
MacGillivray 11kV | Y | 1.8113 | 1.7977 | 2018-01-18 | 1.509 | 1.504 | 2017-06-28 | 0.61382 | 2 | 2.6 | 1.5 | 2 | 0.99249 | 1.8206 | 1.8105 | 1.7729 | 1.7802 | 1.7879 | N | 0.5 | 0.92936 | -
Kingscote 11kV | Y | 3.4435 | 3.3225 | 2018-01-18 | 2.809 | 2.729 | 2017-06-28 | 8.83 | 6.25 | 8 | 0 | 6.25 | 0.96487 | 3.357 | 3.362 | 3.3262 | 3.3244 | 3.3232 | N | 5 | 1.5165 | -
EASTERN HILLS REGION
MOUNT BARKER / MOUNT BARKER SOUTH 66kV | Y | 86.2799 | 86.005 | 2018-01-18 |  |  |  |  | 345 | 361.6 | 149.2 | 345 | 0.99681 | 92.0002 | 93.0526 | 93.2691 | 94.474 | 95.6908 |  |  | 52.2083
Woodside 11kV | Y | 7.8168 | 7.3877 | 2018-02-07 | 6.26 | 6.1009 | 2017-06-20 | 7.0642 | 10 | 13 | 6.9 | 5.6 | 0.9451 | 8.1565 | 8.3268 | 8.4045 | 8.5095 | 8.6207 | N | 6 | 4.8374 | -
Nairne 11kV | Y | 7.7021 | 6.532 | 2018-01-28 | 5.883 | 5.812 | 2017-08-02 | 5.5401 | 7.6 | 9.2 | 4.9 | 7.6 | 0.84809 | 8.5296 | 8.568 | 8.59 | 8.6147 | 8.6511 | N | 5 | 4.648 | -
Brukunga 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.99681 | 0.48544 | 0.48725 | 0.48906 | 0.49087 | 0.4927 | N | 5 | 0.29627 | -
Verdun 11kV | N | - | - | - | - | - | - | 0.76436 | 1 | 1.3 | 0 | 1 | 0.99681 | 1.068 | 1.0719 | 1.0759 | 1.0799 | 1.0839 | N | 5 | 0.99522 | -
Mylor 11kV | Y | 2.2037 | 2.149 | 2018-01-19 | 2.319 | 2.305 | 2017-07-03 | 2.9119 | 3.8 | 4.6 | 0 | 3.8 | 0.97517 | 2.4295 | 2.4783 | 2.4953 | 2.5062 | 2.5072 | N | 5 | 2.1671 | -
Balhannah 33kV | Y | 20.2075 | 19.3144 | 2018-01-28 | 20.742 | 20.447 | 2017-07-17 | 0 | 25 | 35.4 | 18.9 | 24.9504 | 0.9558 | 20.2376 | 19.8977 | 19.211 | 19.5358 | 19.8857 | N | 5 | 12.9988 | -
Stirling East 11kV | Y | 7.2415 | 7.0583 | 2018-01-19 | 8.809 | 8.714 | 2017-08-28 | 5.5257 | 12.5 | 17.2 | 0 | 12.5 | 0.9747 | 8.1495 | 8.4058 | 8.6869 | 8.7941 | 8.8993 | N | 5 | 3.1995 | -
Piccadilly 11kV | Y | 1.709 | 1.6577 | 2018-01-29 | 2.81 | 2.58 | 2017-08-04 | 2.1296 | 3 | 3.9 | 2.25 | 3 | 0.97 | 1.8412 | 1.8471 | 1.8604 | 1.8792 | 1.9005 | N | 5 | 0.9169 | -
Aldgate 11kV | Y | 6.1168 | 6.1053 | 2018-01-19 | 7.689 | 7.689 | 2017-06-06 | 6.4865 | 10 | 12.5808 | 7.1 | 5.1206 | 0.99813 | 6.588 | 6.7292 | 6.8095 | 6.9243 | 7.0459 | N | 5 | 3.3494 | -
Uraidla 33kV | Y | 15.7763 | 15.41 | 2018-01-19 | 19.543 | 19.17 | 2017-08-28 | 39.7 | 25 | 31.4 | 0 | 25 | 0.97678 | 16.7202 | 16.9529 | 17.0198 | 17.1509 | 17.2936 | N | 10 | 7.4658 | -
Uraidla 11kV | Y | 4.3801 | 4.2162 | 2018-01-19 | - | - | - | 4.6947 | 12.5 | 17.2 | 9.2 | 12.5 | 0.96259 | 4.4808 | 4.4777 | 4.481 | 4.49 | 4.5042 | N | 5 | 3.4459 | -
Hahndorf 11kV | Y | 5.099 | 4.8817 | 2018-01-19 | 4.613 | 4.523 | 2017-08-04 | 5.78 | 5 | 6.8 | 0 | 5 | 0.95738 | 5.2944 | 5.3295 | 5.4005 | 5.4539 | 5.5142 | N | 7 | 2.5683 | -
Meadows 11kV | Y | 5.6466 | 5.3501 | 2018-01-18 | 4.275 | 4.198 | 2017-08-04 | 5.916 | 5 | 6.5 | 3.75 | 3.8 | 0.9475 | 5.9664 | 6.0725 | 6.1 | 6.1322 | 6.1175 | N | 5 | 4.6325 | -
Strathalbyn 11kV | Y | 9.9197 | 9.8318 | 2018-01-18 | 8.003 | 8 | 2017-07-03 | 11.65 | 12.5 | 16.7 | 0 | 12.5 | 0.99114 | 11.4046 | 11.6304 | 11.7447 | 11.8665 | 11.9961 | N | 5 | 5.7749 | -
Langhorne Creek 11kV | Y | 3.795 | 3.4635 | 2018-02-23 | 2.249 | 2.035 | 2017-06-22 | 3.8513 | 5 | 6.5 | 3.75 | 3.8 | 0.91266 | 4.0627 | 4.1865 | 4.2697 | 4.3278 | 4.3886 | N | 5 | 1.0883 | -
Milang 11kV | Y | 3.8439 | 3.5854 | 2018-01-27 | 1.925 | 1.882 | 2017-06-21 | 2.8391 | 5 | 6.5 | 3.75 | 3.8558 | 0.93275 | 3.8546 | 3.8864 | 3.9184 | 3.9539 | 3.9933 | N | 5 | 1.6597 | -
Mount Barker 11kV | Y | 22.6682 | 22.64 | 2018-01-18 | 19.56 | 19.5 | 2017-08-03 | 5.6978 | 64 | 72.39 | 38.1 | 64 | 0.99876 | 24.3255 | 24.9696 | 25.4403 | 25.9184 | 26.3936 | N | 7 | 12.5739 | -
ANGAS CREEK 33kV | Y | 18.5053 | 17.8913 | 2018-02-07 |  |  |  |  | 50 | 53.9 | 31.5 | 50 | 0.96682 | 18.9528 | 19.1055 | 19.0997 | 19.2137 | 19.3296 |  |  | 10.6816
Lobethal 11kV | Y | 7.1571 | 6.9146 | 2018-02-07 | 5.753 | 5.638 | 2017-08-17 | 7.929 | 10 | 12.8 | 6.9 | 10 | 0.96612 | 7.1747 | 7.1398 | 7.1107 | 7.1266 | 7.1451 | N | 9 | 3.4434 | -
Gumeracha Weir 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96682 | 0.29874 | 0.29891 | 0.29908 | 0.29926 | 0.29943 | N | 5 | 0.07275 | -
Houghton 7.6kV | Y | 2.1437 | 2.013 | 2018-02-07 | 1.789 | 1.739 | 2017-08-28 | 0 | 3 | 3.6 | 0 | 3 | 0.93904 | 2.3138 | 2.361 | 2.362 | 2.3871 | 2.4117 | N | 5 | 1.6672 | -
Chain of Ponds 11kV | Y | 0.4725 | 0.45833 | 2018-01-21 | 0.371 | 0.342 | 2017-07-27 | 0 | 0.475 | 0.6175 | 0 | 0.475 | 0.97 | 0.48984 | 0.49722 | 0.49956 | 0.50356 | 0.50755 | N | 5 | 0.20628 | -
Hermitage 11kV | Y | 0.14861 | 0.14267 | 2018-01-18 | 0.171 | 0.158 | 2017-08-21 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.96 | 0.2133 | 0.21466 | 0.21366 | 0.21212 | 0.21071 | N | 5 | 0.14382 | -
Deloraine 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96682 | 0.359 | 0.366 | 0.373 | 0.38 | 0.388 | N | 5 | 0.23761 | -
Gumhaven 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96682 | 0.079664 | 0.07971 | 0.079756 | 0.079802 | 0.079848 | N | 5 | 0.01864 | -
Kersbrook 11kV | Y | 0.5091 | 0.493 | 2018-01-19 | 0.508 | 0.505 | 2017-06-30 | 0 | 1 | 1.3 | 0 | 1 | 0.96838 | 0.50791 | 0.51187 | 0.50801 | 0.51179 | 0.51556 | N | 5 | 0.34558 | -
Birdwood 11kV | Y | 2.6151 | 2.533 | 2018-02-07 | 2.37 | 2.361 | 2017-07-15 | 3.3359 | 3 | 3.9 | 0 | 3 | 0.96862 | 2.5994 | 2.6303 | 2.6131 | 2.6368 | 2.6603 | N | 5 | 1.6575 | -
Mount Pleasant 11kV | Y | 2.3606 | 2.2662 | 2018-01-19 | 2.4 | 2.2 | 2017-06-02 | 2.2633 | 2 | 2.6 | 0 | 2 | 0.96 | 2.5388 | 2.5424 | 2.5122 | 2.5185 | 2.5247 | N | 5 | 1.2796 | -
Forreston 11kV | Y | 0.95644 | 0.92775 | 2018-01-19 | 0.474 | 0.436 | 2017-08-14 | 0 | 1 | 1.3 | 0 | 1 | 0.97 | 1.0327 | 1.0358 | 1.0379 | 1.0384 | 1.0393 | N | 5 | 0.48548 | -
Gumeracha 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.96682 | 0.3087 | 0.30888 | 0.30905 | 0.30923 | 0.30941 | Y | 5 | 0.19083 | -
KANMANTOO 11kV | Y | 1.3771 | 1.3611 | 2018-01-28 |  |  |  |  | 3 | 3 | 0 | 3 | 0.98837 | 1.6455 | 1.6384 | 1.6466 | 1.6609 | 1.6761 |  |  | 1.0342 | -
EYRE PENINSULA REGION
WHYALLA CENTRAL 33kV | Y | 65.4353 | 63.4545 | 2017-11-22 |  |  |  |  | 240 | 240 | 120 | 240 | 0.96973 | 76.0006 | 75.7944 | 75.485 | 75.2788 | 75.0725 |  |  | 19.4548
Whyalla City 11kV | Y | 18.4661 | 18.425 | 2018-02-08 | 12.226 | 12.098 | 2017-08-02 | 8.4231 | 20 | 28.5 | 15 | 8.6 | 0.99778 | 18.4679 | 18.1931 | 17.9616 | 17.9962 | 18.0372 | N | 7 | 7.7572 | -
Whyalla Stuart 11kV | Y | 19.1653 | 16.4206 | 2018-02-08 | 10.267 | 10.214 | 2017-08-20 | 10.3979 | 25 | 31 | 16.6 | 8.4 | 0.85679 | 19.7349 | 19.4477 | 19.1718 | 19.1945 | 19.2229 | N | 5 | 6.2126 | -
Whyalla North 11kV | N | - | - | - | - | - | - | 0 | 3 | 2.9 | 1.5 | 2.9 | 1 | 0.7173 | 0.71853 | 0.71922 | 0.71936 | 0.71952 | N | 5 | 0.08497 | -
PORT LINCOLN 33kV | Y | 30.5037 | 30.2617 | 2018-01-18 |  |  |  |  | 75 | 101.4 | 64 | 75 | 0.99207 | 30.621 | 29.881 | 29.4285 | 29.228 | 29.0492 |  |  | 15.1954
Port Lincoln City 11kV | Y | 12.3179 | 12.2889 | 2018-01-18 | 12.006 | 11.737 | 2017-08-02 | 10.1874 | 25 | 29 | 15.2 | 25 | 0.99764 | 11.8017 | 11.4176 | 11.2285 | 11.1426 | 11.0679 | N | 5 | 6.3897 | -
Port Lincoln Docks 11kV | Y | 5.5208 | 5.4532 | 2018-02-16 | 5.826 | 5.8 | 2017-07-20 | 3.3299 | 12.5 | 12.3 | 0 | 5.1 | 0.98775 | 5.3279 | 5.2255 | 5.1498 | 5.0921 | 5.037 | N | 9 | 1.2754 | -
Port Lincoln Marina 11kV | Y | 5.8231 | 5.4029 | 2018-02-09 | 6.514 | 6.38 | 2017-08-08 | 5.9719 | 12.5 | 16.8 | 0 | 12.5 | 0.92783 | 5.6729 | 5.5426 | 5.4485 | 5.4316 | 5.4183 | N | 9 | 2.023 | -
Poonindie 11kV | Y | 0.52585 | 0.49956 | 2018-02-27 | 0.608 | 0.559 | 2017-07-27 | 0.11432 | 1 | 1.3 | 0 | 1 | 0.95 | 0.52726 | 0.52741 | 0.5311 | 0.52859 | 0.52623 | N | 3 | 0.26757 | -
Point Boston 11kV | Y | 1.0999 | 1.045 | 2018-03-20 | 0.9126 | 0.858 | 2017-06-08 | 0 | 2 | 2.6 | 0 | 2 | 0.95013 | 1.0897 | 1.0904 | 1.0942 | 1.0874 | 1.0807 | N | 9 | 0.0235 | -
Tumby Bay 11kV | Y | 2.3292 | 2.328 | 2017-12-28 | 2.78 | 2.559 | 2017-08-02 | 0 | 5 | 5.4 | 3 | 5 | 0.99948 | 2.2794 | 2.1601 | 2.0523 | 2.0086 | 1.9677 | N | 5 | 1.982 | -
Cummins 11kV | Y | 2.5892 | 2.4974 | 2018-02-07 | 2.67 | 2.66 | 2017-06-07 | 0 | 3 | 3.9 | 2.25 | 3 | 0.96455 | 2.5187 | 2.4136 | 2.3419 | 2.3092 | 2.2789 | N | 5 | 1.5258 | -
Uley 11kV | N | - | - | - | - | - | - | 0.21348 | 1 | 1.3 | 0 | 1 | 0.99207 | 0.3024 | 0.3024 | 0.3024 | 0.3024 | 0.3024 | N | 5 | 0.15025 | -
Uley South 11kV | Y | 0.51632 | 0.50083 | 2017-12-05 | 0.512 | 0.471 | 2017-06-01 | 0 | 1.5 | 1.95 | 0 | 1.5 | 0.97 | 0.51715 | 0.51957 | 0.52321 | 0.5221 | 0.52106 | N | 5 | 0 | -
Coffin Bay 11kV | Y | 1.3504 | 1.31 | 2018-01-18 | 0.895 | 0.824 | 2017-06-08 | 0 | 2.5 | 2.7 | 0 | 2.5 | 0.97006 | 1.4053 | 1.3807 | 1.3462 | 1.3402 | 1.3346 | N | 5 | 0.83928 | -
Little Swamp 11kV | Y | 0.24387 | 0.23656 | 2017-11-03 | 0.276 | 0.254 | 2017-06-09 | 0.27612 | 0.3 | 0.39 | 0 | 0.3 | 0.97 | 0.27398 | 0.27215 | 0.26858 | 0.268 | 0.26746 | N | 9 | 0.17447 | -
WUDINNA 66kV | Y | 13.5299 | 13.5148 | 2018-01-18 |  |  |  |  | 50 | 50 | 25 | 50 | 0.99888 | 14.0721 | 13.8027 | 13.6217 | 13.5215 | 13.4244 |  |  | 6.1083
Wudinna 11kV | Y | 1.9351 | 1.934 | 2018-02-07 | 1.503 | 1.491 | 2017-07-06 | 0 | 4 | 5.2 | 4.5 | 4 | 0.99945 | 2.1015 | 2.0515 | 2.0047 | 1.9791 | 1.9544 | N | 5 | 1.0695 | -
Moorkitabie 11kV | Y | 0.58146 | 0.581 | 2018-01-18 | 0.467 | 0.457 | 2017-06-10 | 0 | 1 | 1.3 | 0 | 1 | 0.99922 | 0.70811 | 0.68947 | 0.66936 | 0.6607 | 0.65226 | N | 5 | 0.28919 | -
Tarlton 11kV | Y | 0.51399 | 0.465 | 2018-02-07 | 0.476 | 0.35 | 2017-07-28 | 0.75 | 0.5 | 0.65 | 0 | 0.5 | 0.90469 | 0.76082 | 0.74439 | 0.73154 | 0.72444 | 0.71746 | Y | 5 | 0.24874 | -
Streaky Bay 11kV | Y | 2.8287 | 2.742 | 2018-01-18 | 1.93 | 1.929 | 2017-07-04 | 0 | 5 | 6.5 | 3.75 | 3.8 | 0.96935 | 3.147 | 3.0262 | 2.9665 | 2.9211 | 2.8776 | N | 5 | 1.8667 | -
Ceduna 11kV | Y | 6.5514 | 6.3503 | 2017-12-18 | 5.594 | 5.505 | 2017-06-04 | 0 | 10 | 14.2 | 7.5 | 10 | 0.96931 | 6.8163 | 6.7633 | 6.7255 | 6.716 | 6.706 | N | 5 | 2.6342 | -
Polda 11kV | Y | 0.75177 | 0.751 | 2018-01-28 | 0.64 | 0.627 | 2017-08-26 | 0 | 1 | 1.3 | 0 | 1 | 0.99898 | 0.86595 | 0.83416 | 0.81069 | 0.79901 | 0.78774 | N | 5 | 0.52711 | -
YADNARIE 66kV | Y | 7.3708 | 7.1996 | 2018-01-18 |  |  |  |  | 40 | 46.4 | 27.4 | 40 | 0.97678 | 8.2143 | 7.9835 | 7.829 | 7.7517 | 7.6805 |  |  | 4.2113
Cleve 11kV | Y | 2.3501 | 2.3492 | 2018-01-18 | 2.267 | 2.257 | 2017-07-20 | 0 | 5 | 6.5 | 3.5 | 4.9905 | 0.9996 | 2.4485 | 2.3345 | 2.2813 | 2.2503 | 2.2275 | N | 5 | 1.3527 | -
Boothby 33kV | Y | 0.71447 | 0.65957 | 2017-11-29 | 0.716 | 0.659 | 2017-07-20 | 0 | 3 | 3.9 | 0 | 3 | 0.92316 | 0.695 | 0.67222 | 0.65537 | 0.6462 | 0.63901 | N | 5 | 0.40097 | -
Arno Bay 11kV | Y | 0.71447 | 0.65957 | 2017-11-29 | 0.716 | 0.659 | 2017-07-20 | 0 | 3 | 3.9 | 0 | 3 | 0.92316 | 0.695 | 0.67222 | 0.65537 | 0.6462 | 0.63901 | N | 5 | 0.2942 | -
Cowell 11kV | Y | 1.838 | 1.815 | 2018-01-18 | 1.4 | 1.399 | 2017-08-04 | 0 | 3 | 3.9 | 0 | 3 | 0.98747 | 2.0336 | 1.9401 | 1.8829 | 1.8515 | 1.8266 | N | 5 | 1.112 | -
Cleve 33kV | Y | 2 | 2 | 2018-01-19 | 1.63 | 1.6 | 2017-06-02 | 4.5 | 12.5 | 17.8 | 0 | 12.5 | 1 | 2.188 | 2.1317 | 2.0701 | 2.0498 | 2.0176 | N | 5 | 1.279 | -
Darke Peak 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.97678 | 0.64523 | 0.6331 | 0.62119 | 0.60951 | 0.59805 | N | 5 | 0.12594 | -
Rudall 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.97678 | 0.092176 | 0.090442 | 0.088742 | 0.087073 | 0.085435 | N | 5 | 0.0581 | -
Caralue 11kV | Y | 2.121 | 1.9979 | 2018-02-07 | 2.028 | 1.856 | 2017-08-04 | 0 | 2.5 | 3.25 | 0 | 2.1 | 0.94194 | 2.3704 | 2.3055 | 2.2446 | 2.2171 | 2.1959 | N | 5 | 0.63728 | -
LOCK REG 66kV | N | - | - | - | - | - | - |  | 20 | 25 | 0 | 20 |  | 0.82958 | 0.81398 | 0.79867 | 0.78366 | 0.76892 | N | 5 | - | -
Lock 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.97678 | 0.82958 | 0.81398 | 0.79867 | 0.78366 | 0.76892 | N | 5 | 0.2311 | -
MURRAYLANDS
MOBILONG 33kV | Y | 40.3112 | 37.6075 | 2017-11-29 |  |  |  |  | 120 | 114.3 | 57.2 | 120 | 0.93293 | 44.3488 | 44.8238 | 45.228 | 45.5566 | 45.7826 |  |  | 13.495
Murray Bridge North 11kV | Y | 18.0215 | 17.4707 | 2017-11-29 | 14.153 | 13.491 | 2017-06-07 | 8.7371 | 20 | 26.0138 | 14.8 | 6.937 | 0.96943 | 18.5956 | 18.7883 | 18.9924 | 19.1297 | 19.224 | N | 6 | 5.3685 | -
Murray Bridge South 11kV | Y | 15.9698 | 15.3518 | 2018-01-18 | 12.879 | 12.68 | 2017-08-02 | 5.4791 | 20 | 28.5 | 15 | 7.6 | 0.9613 | 16.4666 | 16.5143 | 16.5085 | 16.5935 | 16.6437 | N | 6 | 6.363 | -
Mypolonga 11kV | Y | 2.6776 | 2.571 | 2018-01-28 | 1.199 | 1.173 | 2017-06-29 | 0 | 4 | 4.8 | 2.56 | 2 | 0.96019 | 2.7767 | 2.7829 | 2.7933 | 2.805 | 2.8105 | N | 4 | 0.97538 | -
Monarto South 11kV | Y | 3.9058 | 3.359 | 2018-01-18 | 4.472 | 4 | 2017-06-22 | 1.7221 | 12.5 | 14.5 | 0 | 12.5 | 0.86 | 4.7146 | 4.8576 | 4.9799 | 5.0514 | 5.1104 | N | 6 | 0.75812 | -
Monarto Central 11kV | Y | 2.9693 | 2.794 | 2018-01-12 | - | - | - | 2.4619 | 6.25 | 8.1 | 0 | 6.25 | 0.94098 | 3.0333 | 3.1037 | 3.157 | 3.1811 | 3.1969 | N | 4 | 0.03 | -
MANNUM 33kV | Y | 12.6187 | 12.265 | 2018-01-28 |  |  |  |  | 40 | 40 | 21 | 40 | 0.97197 | 14.1887 | 14.1317 | 14.1324 | 14.2001 | 14.2745 |  |  | 5.8668
Belvedere Road 7.6kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.97197 | 0.10863 | 0.10886 | 0.10908 | 0.10931 | 0.10953 | N | 7 | 0.01826 | -
Caloote 11kV | Y | 1.9053 | 1.7406 | 2018-01-28 | 1.36 | 1.334 | 2017-07-28 | 0 | 3 | 3.9 | 2.25 | 3 | 0.91357 | 1.8475 | 1.7817 | 1.7429 | 1.7326 | 1.724 | N | 7 | 0.86706 | -
Mannum Town 7.6kV | Y | 4.4927 | 4.2681 | 2018-01-18 | 2.841 | 2.801 | 2017-06-02 | 0 | 6 | 7.8 | 4.5 | 6 | 0.95 | 4.7033 | 4.6845 | 4.6593 | 4.6972 | 4.7372 | N | 7 | 2.0398 | -
Cambrai 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0.75 | 1 | 0.97197 | 0.98756 | 0.9896 | 0.99165 | 0.99371 | 0.99577 | N | 4 | 0.4715 | -
Palmer 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.97197 | 0.029627 | 0.029688 | 0.02975 | 0.029811 | 0.029873 | N | 4 | 0.06082 | -
Pellaring Flat 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.97197 | 0.098756 | 0.09896 | 0.099165 | 0.099371 | 0.099577 | N | 4 | 0.01504 | -
Teal Flat 11kV | N | - | - | - | - | - | - | 0 | 3 | 3.9 | 3 | 3 | 0.97197 | 3.3182 | 3.3251 | 3.332 | 3.3389 | 3.3458 | N | 4 | 0.75714 | -
Walker Flat 11kV | Y | 1.2367 | 1.185 | 2018-01-27 | 0.671 | 0.656 | 2017-07-28 | 0 | 2 | 2 | 0 | 2 | 0.95816 | 1.2997 | 1.2673 | 1.2434 | 1.2381 | 1.2336 | N | 4 | 0.43561 | -
Nildottie 11kV | Y | 2.0052 | 1.984 | 2018-01-05 | 1.343 | 1.343 | 2017-08-17 | 0 | 3.8 | 4.94 | 0 | 3.8 | 0.98941 | 1.9829 | 1.9809 | 1.9852 | 1.9954 | 2.0063 | N | 5 | 0.39612 | -
Punyelroo 11kV | Y | 0.46131 | 0.447 | 2018-01-27 | 0.33 | 0.322 | 2017-06-10 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.96898 | 0.50599 | 0.49822 | 0.49046 | 0.49 | 0.48976 | N | 4 | 0.15765 | -
TAILEM BEND 33kV | Y | 21.1643 | 20.8799 | 2018-01-18 |  |  |  |  | 50 | 60 | 32.5 | 50 | 0.98656 | 25.0854 | 24.9259 | 24.8027 | 24.6951 | 24.5964 |  |  | 7.2999
Tailem Bend Town 11kV | N | - | - | - | - | - | - | 0 | 3 | 3.9 | 2.25 | 3 | 0.98656 | 3.1253 | 3.1212 | 3.117 | 3.1128 | 3.1087 | N | 4 | 1.745 | -
Jervois 11kV | Y | 1.6885 | 1.542 | 2018-02-09 | 1.274 | 1.197 | 2017-07-20 | 0.48348 | 3.8 | 4.6 | 0 | 3.8 | 0.91322 | 1.6621 | 1.6305 | 1.6008 | 1.5893 | 1.5786 | N | 5 | 0.60163 | -
Woods Point 11kV | Y | 3.5189 | 3.27 | 2018-01-18 | 2.821 | 2.63 | 2017-06-20 | 3.1277 | 6.25 | 8.1 | 0 | 6.25 | 0.92926 | 2.0168 | 1.9734 | 1.9326 | 1.9092 | 1.8874 | N | 7 | 0.72983 | -
Whitesands 11kV
Coomandook 11kV | Y | 0.36702 | 0.364 | 2018-01-28 | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.99177 | 0.52531 | 0.51274 | 0.49556 | 0.49079 | 0.48619 | N | 4 | 0.15717
Ki Ki 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.98656 | 0.10743 | 0.10729 | 0.10715 | 0.107 | 0.10686 | N | 4 | 0.0145 | -
Coonalpyn 11kV | Y | 0.3975 | 0.3755 | 2018-01-28 | 0.368 | 0.357 | 2017-06-01 | 0 | 1 | 1.3 | 0 | 1 | 0.94466 | 0.53413 | 0.51147 | 0.48947 | 0.48153 | 0.47398 | N | 1 | 0.19662 | -
COONALPYN REG 33kV | N | - | - | - | - | - | - | 0 | 10 | 12.5 | 0 | 8.3 | 0.94466 | 6.2063 | 6.0663 | 5.9465 | 5.8816 | 5.8197 | N | 4 | - | -
Binnies 11kV | Y | 0.67009 | 0.661 | 2017-11-13 | 0.35 | 0.34 | 2017-07-29 | 0 | 2 | 2.6 | 0 | 2 | 0.98643 | 0.74995 | 0.74714 | 0.7446 | 0.73893 | 0.73344 | N | 4 | 0.006 | -
Meningie 11kV | Y | 2.031 | 1.9673 | 2018-01-28 | 1.987 | 1.971 | 2017-06-23 | 0 | 5 | 6.5 | 3.75 | 5 | 0.96864 | 2.1536 | 2.0528 | 1.9749 | 1.9362 | 1.8996 | N | 10 | 1.0261 | -
CAMPBELL PARK PT REG 33kV | N | - | - | - | - | - | - | 0 | 5.7 | 7.4305 | 0 | 5.7 |  | 2.7686 | 2.7549 | 2.7375 | 2.7249 | 2.7126 | N | 4 | - | -
Campbell Park 11kV | N | - | - | - | - | - | - | 0.72205 | 1.5 | 1.95 | 1.5 | 1.5 | 0.98656 | 1.465 | 1.463 | 1.4611 | 1.4591 | 1.4572 | N | 4 | 0.11687 | -
Narrung 11kV | Y | 0.42868 | 0.41582 | 2017-11-11 | 0.839 | 0.756 | 2017-06-17 | 0.40156 | 4 | 3.9 | 2.25 | 3.9 | 0.97 | 1.3036 | 1.2919 | 1.2765 | 1.2658 | 1.2555 | N | 5 | 0.06965 | -
Sherlock 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.98656 | 0.0293 | 0.029261 | 0.029222 | 0.029183 | 0.029144 | N | 4 | 0.03846 | -
SHERLOCK REG 33kV | Y | - | - | - | - | - | - | 0 | 20 | 25 | 0 | 20 |  | 5.0881 | 5.0233 | 4.9657 | 4.9325 | 4.9007 | N | 6 | - | -
Karoonda 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0.75 | 1 | 0.98656 | 0.78133 | 0.78029 | 0.77925 | 0.77821 | 0.77717 | N | 4 | 0.39597 | -
Peake 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.98656 | 0.15627 | 0.15606 | 0.15585 | 0.15564 | 0.15543 | N | 4 | 0.0882 | -
Jabuk 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.98656 | 0.078133 | 0.078029 | 0.077925 | 0.077821 | 0.077717 | N | 4 | 0.009 | -
GERANIUM REG 33kV | Y | - | - | - | - | - | - | 0 | 10 | 12.5 | 0 | 8.3261 |  | 4.0724 | 4.0089 | 3.9527 | 3.9209 | 3.8904 | N | 6 | - | -
Geranium 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.98656 | 0.1465 | 0.1463 | 0.14611 | 0.14591 | 0.14572 | N | 4 | 0.03892 | -
Lameroo 11kV | N | - | - | - | - | - | - | 0 | 2 | 2.6 | 1.5 | 2 | 0.98656 | 1.3283 | 1.3265 | 1.3247 | 1.323 | 1.3212 | N | 4 | 0.58079 | -
Parilla 11kV | Y | 0.5087 | 0.48327 | 2018-03-24 | 0.368 | 0.338 | 2017-06-28 | 0 | 1 | 1.3 | 0 | 1 | 0.95 | 0.98238 | 0.97712 | 0.97063 | 0.96301 | 0.95561 | N | 5 | 0.03924 | -
Pinnaroo South 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.98656 | 0.1172 | 0.11704 | 0.11689 | 0.11673 | 0.11658 | N | 4 | 0.0052 | -
Pinnaroo 11kV | Y | 1.4813 | 1.3941 | 2018-01-28 | 0.415 | 0.401 | 2017-07-20 | 0 | 2 | 2.6 | 1.5 | 2 | 0.94116 | 1.498 | 1.4419 | 1.3944 | 1.3723 | 1.3513 | N | 4 | 0.52665 | -
MID NORTH and YORKE PENINSULA
ARDROSSAN WEST 33kV | Y | 9.8603 | 9.7483 | 2018-01-18 |  |  |  |  | 50 | 62 | 32.5 | 50 | 0.98865 | 11.0488 | 10.7915 | 10.6253 | 10.5345 | 10.4531 |  |  | 6.8695
Ardrossan 11kV | Y | 2.0225 | 1.972 | 2018-01-18 | 1.59 | 1.575 | 2017-06-29 | 0 | 3 | 3.9 | 3 | 3 | 0.97505 | 2.2951 | 2.2711 | 2.2422 | 2.2351 | 2.229 | N | 3 | 1.2034 | -
Maitland 11kV | Y | 3.3633 | 3.267 | 2018-01-27 | 3.074 | 3.066 | 2017-06-10 | 0 | 5 | 7.125 | 3.75 | 5 | 0.97137 | 3.3371 | 3.1727 | 3.0672 | 3.0118 | 2.9607 | N | 2 | 2.337 | -
James Well 7.6kV | N | - | - | - | - | - | - | 0 | 0.7 | 0.91 | 0 | 0.7 | 0.98865 | 0.37463 | 0.36583 | 0.35724 | 0.34886 | 0.34066 | N | 2 | 0.15253 | -
Black Point 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.98865 | 0.52274 | 0.51047 | 0.49848 | 0.48678 | 0.47535 | N | 2 | 0.17563 | -
Port Julia 11kV | Y | 0.2788 | 0.27044 | 2018-01-01 | 0.442 | 0.407 | 2017-06-10 | 0 | 1 | 1.3 | 0 | 1 | 0.97 | 0.25795 | 0.24202 | 0.23618 | 0.22981 | 0.2239 | N | 2 | 0.25359 | -
Port Vincent 11kV | Y | 1.1476 | 1.1132 | 2018-01-18 | 1.194 | 1.099 | 2017-06-10 | 0 | 2 | 2.6 | 1.5 | 2 | 0.97 | 1.5751 | 1.5583 | 1.5359 | 1.5299 | 1.5245 | N | 2 | 0.72329 | -
PORT VINCENT 33kV | Y | 2.2216 | 2.1557 | 2018-03-31 | 2.1578 | 2.0636 | 2017-06-03 | 0 | 20 | 25 | 0 | 20 | 0.97032 | 2.4505 | 2.4329 | 2.3818 | 2.3783 | 2.3754 | N | 2 | - | -
Curramulka 7.6kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.98865 | 0.234 | 0.242 | 0.249 | 0.257 | 0.265 | Y | 2 | 0.14708 | -
Curramulka South 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.98865 | 0.026406 | 0.025786 | 0.025181 | 0.02459 | 0.024012 | N | 2 | 0.01512 | -
Minlaton 11kV | Y | 1.6004 | 1.5364 | 2018-01-18 | 1.728 | 1.589 | 2017-08-29 | 0 | 2 | 2.6 | 1.5 | 2 | 0.96 | 1.5241 | 1.4283 | 1.3635 | 1.3305 | 1.2998 | N | 2 | 1.2391 | -
DALRYMPLE 33kV | Y | 6.2223 | 6.2215 | 2018-01-18 |  |  |  |  | 50 | 50 | 25 | 50 | 0.99987 | 8.0193 | 7.808 | 7.6149 | 7.529 | 7.4496 |  |  | 4.4615
Port Giles 11kV | Y | 1.3777 | 1.169 | 2018-01-07 | 1.86 | 1.71 | 2017-07-19 | 0.20709 | 2.5 | 3.25 | 0 | 2.5 | 0.84853 | 2.045 | 2.0394 | 2.0328 | 2.02 | 2.0076 | N | 2 | 0.19594 | -
Stansbury 11kV | Y | 1.1373 | 1.1 | 2018-01-18 | 0.988 | 0.968 | 2017-06-10 | 0 | 2.5 | 2.7 | 0 | 2.5 | 0.96718 | 1.2616 | 1.2417 | 1.199 | 1.1776 | 1.1574 | N | 7 | 0.68764 | -
Edithburgh 11kV | Y | 1.1298 | 1.0507 | 2018-01-18 | 1.21 | 1.183 | 2017-06-10 | 1.3888 | 2.5 | 3 | 0 | 2.5 | 0.93 | 1.2208 | 1.1369 | 1.0769 | 1.0533 | 1.0315 | N | 2 | 0.94721 | -
Yorketown 11kV | Y | 1.3292 | 1.3292 | 2018-01-18 | 1.697 | 1.56 | 2017-08-04 | 0.7106 | 2 | 2.6 | 1.5 | 2 | 1 | 1.1935 | 1.1187 | 1.0606 | 1.0393 | 1.0196 | N | 9 | 0.97293 | -
Warooka 11kV | Y | 2.1097 | 2.058 | 2018-01-27 | 1.29 | 1.285 | 2017-06-09 | 0.12111 | 5 | 5.4 | 3 | 5 | 0.97551 | 2.294 | 2.2122 | 2.1313 | 2.0981 | 2.0671 | N | 2 | 1.1693 | -
Marion Bay 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.99987 | 0.65178 | 0.638 | 0.6245 | 0.6113 | 0.59837 | N | 2 | 0.2731 | -
BRINKWORTH 33kV | Y | 4.6943 | 4.6903 | 2018-01-28 |  |  |  |  | 20 | 24.6 | 13.7 | 10 | 0.99914 | 4.7549 | 4.6889 | 4.5771 | 4.5518 | 4.5276 |  |  | 2.6712
Brinkworth Town 11kV | Y | 0.85737 | 0.78878 | 2018-01-28 | 0.683 | 0.674 | 2017-06-03 | 0.95263 | 3 | 3.9 | 0 | 3 | 0.92 | 0.82162 | 0.79083 | 0.75491 | 0.74631 | 0.73815 | N | 6 | 0.40362 | -
Kybunga 11kV | Y | 0.057158 | 0.055451 | 2018-02-09 | 0.064 | 0.063 | 2017-06-08 | 0 | 0.1 | 0.13 | 0 | 0.1 | 0.97014 | 0.050909 | 0.049772 | 0.047543 | 0.047359 | 0.047181 | N | 6 | 0.02516 | -
Hoyleton 11kV | Y | 0.07621 | 0.075199 | 2017-11-28 | 0.088 | 0.089 | 2017-08-29 | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.98673 | 0.088662 | 0.087124 | 0.083656 | 0.083432 | 0.083214 | N | 6 | 0.05134 | -
Halbury 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.99914 | 0.081692 | 0.080111 | 0.078561 | 0.077041 | 0.07555 | N | 6 | 0.0555 | -
Collinsfield 11kV | Y | 0.45726 | 0.45726 | 2017-11-28 | 0.5705 | 0.568 | 2017-06-14 | 0.92879 | 2.5 | 2.7 | 0 | 2.5 | 1 | 0.50814 | 0.49824 | 0.47789 | 0.47623 | 0.47463 | N | 6 | 0.2702 | -
Spalding 11kV | Y | 0.97168 | 0.97168 | 2018-01-28 | 0.88 | 0.873 | 2017-06-30 | 0 | 2 | 2.6 | 1.5 | 2 | 1 | 0.92022 | 0.88719 | 0.84446 | 0.83601 | 0.82797 | N | 6 | 0.49565 | -
Georgetown 11kV | Y | 0.13337 | 0.13333 | 2018-01-17 | 0.134 | 0.132 | 2017-06-07 | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.99974 | 0.20071 | 0.20006 | 0.19659 | 0.19451 | 0.19255 | N | 6 | 0.07484 | -
Gulnare 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.99914 | 0.090769 | 0.089013 | 0.08729 | 0.085601 | 0.083944 | N | 6 | 0.01798 | -
HUMMOCKS 33kV | Y | 14.7456 | 14.1014 | 2018-02-07 |  |  |  |  | 50 | 50 | 25 | 50 | 0.95631 | 14.7518 | 14.673 | 14.6455 | 14.5789 | 14.5182 |  |  | 4.5117
BOWMANS PT REG 33kV | N | - | - | - | - | - | - | 0 | 11.4 | 14.861 | 0 | 11.4 |  | 3.0899 | 2.9929 | 2.9187 | 2.8763 | 2.8363 | N | 3 | - | -
Balaklava 7.6kV | Y | 2.9486 | 2.8227 | 2018-02-08 | 2.096 | 2.079 | 2017-08-26 | 0 | 5 | 5 | 2.78 | 5 | 0.95728 | 3.0899 | 2.9929 | 2.9187 | 2.8763 | 2.8363 | N | 3 | 1.2311 | -
Ninnes 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.95631 | 0.85788 | 0.85445 | 0.85104 | 0.84763 | 0.84425 | N | 2 | 0.5524 | -
PASKEVILLE REG 33kV | N | - | - | - | - | - | - | 0 | 20 | 25 | 0 | 20 |  | 0.29826 | 0.29707 | 0.29588 | 0.2947 | 0.29352 | N | 2 | - | -
Paskeville 11kV | N | - | - | - | - | - | - | 0 | 0.95 | 1.235 | 0.7125 | 0.95 | 0.95631 | 0.29826 | 0.29707 | 0.29588 | 0.2947 | 0.29352 | N | 2 | 0.24785 | -
Port Clinton 11kV | Y | 0.44964 | 0.41817 | 2018-01-18 | 0.457 | 0.42 | 2017-06-11 | 0 | 1 | 1.3 | 0 | 1 | 0.93 | 0.52274 | 0.50288 | 0.47922 | 0.47158 | 0.46437 | N | 2 | 0.36826 | -
Dowlingville 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.95631 | 0.038128 | 0.037976 | 0.037824 | 0.037673 | 0.037522 | N | 2 | 0.02448 | -
KADINA EAST 33kV | Y | 26.6189 | 25.3859 | 2018-01-19 |  |  |  |  | 120 | 120 | 60 | 120 | 0.95368 | 26.9087 | 26.7179 | 26.8048 | 26.9756 | 27.1655 |  |  | 13.3491
Kadina 11kV | Y | 8.4215 | 8.0354 | 2018-02-08 | 6.394 | 6.308 | 2017-08-02 | 0 | 12.5 | 16 | 8.8 | 5 | 0.95415 | 8.6817 | 8.6769 | 8.7131 | 8.7713 | 8.8339 | N | 7 | 4.3309 | -
Moonta 11kV | Y | 8.7261 | 8.4643 | 2018-01-19 | 6.093 | 5.605 | 2017-06-10 | 0 | 10 | 12.8 | 7.1 | 10 | 0.97 | 8.605 | 8.437 | 8.4067 | 8.4229 | 8.4466 | N | 6 | 5.0408 | -
Wallaroo 11kV | Y | 8.3488 | 7.93 | 2018-01-19 | 5.319 | 5.227 | 2017-07-07 | 0 | 12.5 | 16.2 | 9 | 5 | 0.94984 | 8.1333 | 8.0893 | 8.1361 | 8.2127 | 8.2957 | N | 6 | 3.8653 | -
WATERLOO 33kV | Y | 8.8035 | 8.586 | 2018-02-07 |  |  |  |  | 50 | 50 | 25 | 50 | 0.9753 | 8.7986 | 8.5987 | 8.45 | 8.3819 | 8.3192 |  |  | 4.4399
Marrabel 11kV | Y | 0.88233 | 0.87 | 2018-01-28 | - | - | - | 0.99928 | 2 | 2.6 | 0 | 2 | 0.98602 | 0.94249 | 0.86288 | 0.77618 | 0.75785 | 0.74059 | N | 2 | 0.61005 | -
Eudunda 11kV | Y | 1.8572 | 1.7644 | 2018-01-19 | 1.727 | 1.59 | 2017-08-20 | 0.54074 | 2 | 2.4 | 0 | 2 | 0.95 | 1.7694 | 1.6904 | 1.6334 | 1.6032 | 1.5748 | N | 6 | 0.66724 | -
Robertstown 11kV | N | - | - | - | - | - | - | 0.57158 | 1 | 1.3 | 0 | 1 | 0.9753 | 0.9183 | 0.90564 | 0.89315 | 0.88083 | 0.86869 | N | 6 | 0.38461 | -
Auburn 11kV | N | - | - | - | - | - | - | 0 | 3 | 3.9 | 2.25 | 3 | 0.9753 | 3.214 | 3.1697 | 3.126 | 3.0829 | 3.0404 | N | 6 | 1.5808 | -
Riverton 11kV | Y | 1.9053 | 1.7528 | 2018-02-07 | 1.82 | 1.793 | 2017-06-27 | 1.1412 | 3 | 3.9 | 0 | 3 | 0.92 | 2.0204 | 1.9596 | 1.9161 | 1.8935 | 1.8724 | N | 2 | 0.92736 | -
Waterloo Town 11kV | Y | 0.4669 | 0.42955 | 2018-01-19 | 0.19 | 0.19 | 2017-07-20 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.92 | 0.5123 | 0.50325 | 0.49327 | 0.48877 | 0.48445 | N | 6 | 0.05399 | -
CLARE NORTH 33kV | Y | 11.8836 | 11.2729 | 2018-02-07 |  |  |  |  | 50 | 50 | 25 | 50 | 0.94861 | 12.5117 | 12.2924 | 12.1275 | 12.0127 | 11.9045 |  |  | 5.1335
Clare 11kV | Y | 8.9597 | 8.5311 | 2018-02-07 | 6.818 | 6.705 | 2017-08-02 | 0 | 10 | 12.6 | 7.1 | 5 | 0.95217 | 9.051 | 8.9034 | 8.81 | 8.7581 | 8.7107 | N | 9 | 4.1709 | -
CLARE PT REG 33kV | N | - | - | - | - | - | - | 0 | 11.4 | 14.861 | 0 | 11.4 |  | 2.9901 | 2.9263 | 2.8604 | 2.801 | 2.7433 | N | 6 | - | -
BURRA PT REG 33kV | N | - | - | - | - | - | - | 0 | 5.7 | 7.4305 | 0 | 5.7 |  | 2.9901 | 2.9263 | 2.8604 | 2.801 | 2.7433 | N | 6 | 0.96111 | -
Burra 11kV | Y | 2.9714 | 2.8741 | 2018-02-09 | 2.958 | 2.903 | 2017-08-28 | 0 | 10 | 11.4 | 5.7 | 4.4 | 0.96725 | 2.9901 | 2.9263 | 2.8604 | 2.801 | 2.7433 | N | 6 | 0.961 | -
DORRIEN 33kV | Y | 60.1902 | 56.545 | 2018-02-08 |  |  |  |  | 180 | 216 | 156 | 180 | 0.93944 | 62.2003 | 62.428 | 62.8947 | 63.1093 | 63.3456 |  |  | 21.868
Barossa South TF1 11kV | Y | 2.8293 | 2.79 | 2018-02-07 | 2.93 | 2.89 | 2017-08-09 | 2.9098 | 6.25 | 8.9062 | 0 | 6.25 | 0.98611 | 2.9947 | 3.0109 | 3.0549 | 3.0643 | 3.0746 | N | 9 | 0.70184 | -
Barossa South TF2 11kV | Y | 4.3428 | 3.86 | 2018-02-23 | 2.59 | 2.27 | 2017-07-13 | 4.9012 | 6.25 | 8.1 | 0 | 6.25 | 0.88883 | 6.684 | 6.7973 | 6.9195 | 6.9606 | 7.0023 | N | 9 | 0.04704 | -
Angaston 11kV | Y | 14.4334 | 14.0364 | 2018-02-06 | 13.066 | 12.916 | 2017-08-08 | 7.348 | 25 | 28.956 | 15.24 | 25 | 0.97249 | 14.8143 | 14.8711 | 14.9979 | 15.0625 | 15.1313 | N | 9 | 4.8076 | -
Gomersal North 11kV | Y | 0.42297 | 0.38913 | 2018-01-26 | 0.135 | 0.125 | 2017-07-26 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.92 | 0.42512 | 0.43164 | 0.43898 | 0.44021 | 0.44145 | N | 9 | 0 | -
Dorrien TF4 11kV | Y | 8.705 | 8.2786 | 2018-02-08 | 6.1 | 5.855 | 2017-07-18 | 9.445 | 12.5 | 13.6 | 0 | 12.5 | 0.95102 | 8.5913 | 8.5647 | 8.6317 | 8.64 | 8.6525 | N | 9 | 2.995 | -
Dorrien TF5 11kV | Y | 3.4686 | 3.2694 | 2018-02-07 | 2.67 | 2.52 | 2017-06-02 | 4.1424 | 12.5 | 13.6 | 0 | 12.5 | 0.94257 | 3.8393 | 3.8254 | 3.8297 | 3.8577 | 3.886 | N | 9 | 1.7237 | -
Nuriootpa 11kV | Y | 11.4582 | 10.9463 | 2018-02-08 | 8.571 | 8.401 | 2017-08-28 | 9.4369 | 12.5 | 13.4 | 0 | 5.1 | 0.95533 | 11.7588 | 11.7232 | 11.7739 | 11.8205 | 11.872 | N | 7 | 4.2896 | -
Stockwell TF1 11kV | Y | 2.0506 | 2.03 | 2018-01-19 | 1.58 | 1.57 | 2017-08-05 | 2.4775 | 6.25 | 8.9062 | 0 | 6.25 | 0.98995 | 2.0278 | 1.9792 | 1.981 | 1.9678 | 1.9564 | N | 9 | 1.3229 | -
Stockwell TF2 11kV | Y | 5.2178 | 4.95 | 2018-03-07 | 4.28 | 4.27 | 2017-08-23 | 5.7356 | 6.25 | 7.9 | 0 | 6.25 | 0.94868 | 5.2117 | 5.2777 | 5.3624 | 5.3951 | 5.4289 | N | 9 | 0.62278 | -
Lyndoch 11kV | Y | 3.1818 | 3.0088 | 2018-02-08 | 1.948 | 1.939 | 2017-08-04 | 3.74 | 3.8 | 4.3 | 0 | 3.8 | 0.94564 | 3.099 | 3.1001 | 3.1048 | 3.1199 | 3.1359 | N | 6 | 1.4996 | -
Lyndoch South 7.6kV | Y | 0.4344 | 0.41964 | 2018-02-07 | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.96603 | 0.51781 | 0.52071 | 0.52012 | 0.52392 | 0.52779 | N | 6 | 0.10668 | -
Williamstown 11kV | Y | 0.91071 | 0.86518 | 2018-01-18 | 0.668 | 0.614 | 2017-06-07 | 0.73448 | 2.5 | 3 | 0 | 2.5 | 0.95 | 1.0307 | 1.039 | 1.046 | 1.0542 | 1.0626 | N | 6 | 0.42209 | -
Williamstown South 11kV | Y | 2.6674 | 2.454 | 2018-01-28 | 1.052 | 1.044 | 2017-08-29 | 2.2724 | 3.8 | 4.3 | 0 | 3.8 | 0.92 | 2.8479 | 2.8097 | 2.8064 | 2.8074 | 2.8102 | N | 6 | 1.4522 | -
TEMPLERS 33kV | Y | 29.6114 | 28.5941 | 2018-02-07 |  |  |  |  | 120 | 147.6 | 79.8 | 120 | 0.96565 | 31.3756 | 31.6885 | 31.8194 | 31.9128 | 31.8104 |  |  | 13.4506
Freeling 11kV | N | - | - | - | - | - | - | 0.4507 | 3 | 3.9 | 2.25 | 3 | 0.96565 | 0.38539 | 0.3846 | 0.38381 | 0.38302 | 0.38223 | N | 6 | 0.30773 | -
Freeling North 11kV | Y | 2.8769 | 2.6756 | 2018-01-28 | 2.029 | 2.019 | 2017-08-20 | 2.8938 | 3.8 | 4.3 | 0 | 3.8 | 0.93 | 3.8031 | 3.7903 | 3.7661 | 3.752 | 3.7154 | N | 6 | 1.377 | -
Kapunda TF1 11kV | Y | 4.0316 | 3.8785 | 2018-02-08 | 3.826 | 3.7077 | 2017-06-26 | 4.0324 | 12.5 | 14.8 | 0 | 12.5 | 0.96202 | 4.397 | 4.5109 | 4.5462 | 4.5936 | 4.6113 | N | 7 | 0.95599 | -
Kapunda TF2 11kV | Y | 2.6507 | 2.5967 | 2018-01-28 | 2.19 | 2.189 | 2017-08-04 | 2.9301 | 12.5 | 17.4 | 0 | 12.5 | 0.97961 | 2.7919 | 2.7818 | 2.7739 | 2.7806 | 2.7713 | N | 7 | 1.3353 | -
Wasleys 11kV | N | - | - | - | - | - | - | 1.1397 | 2 | 2.6 | 1.5 | 2 | 0.96565 | 2.3123 | 2.3076 | 2.3028 | 2.2981 | 2.2934 | N | 3 | 0.86924 | -
Mallala 11kV | Y | 4.7631 | 4.3821 | 2018-01-18 | 3.183 | 2.92 | 2017-08-20 | 0.47435 | 6 | 7.8 | 4.5 | 6 | 0.92 | 4.7867 | 4.7564 | 4.7133 | 4.6956 | 4.6499 | N | 3 | 1.8509 | -
Sandy Creek 11kV | Y | 2.4578 | 2.3103 | 2018-01-28 | 0.401 | 0.395 | 2017-06-20 | 0 | 3 | 3.9 | 0 | 3 | 0.94 | 2.64 | 2.8282 | 2.8378 | 2.8278 | 2.8195 | N | 9 | 1.4041 | -
Gawler Belt TF1 11kV | Y | 4.8525 | 4.4751 | 2018-02-08 | 3.575 | 3.4351 | 2017-07-18 | 4.9646 | 12.5 | 14.6 | 0 | 12.5 | 0.92223 | 5.2233 | 5.2199 | 5.2442 | 5.2388 | 5.2031 | N | 6 | 2.3856 | -
Gawler Belt TF2 11kV | Y | 4.6922 | 4.5326 | 2018-01-28 | 3.16 | 3.1018 | 2017-08-03 | 5.0476 | 12.5 | 14.6 | 0 | 12.5 | 0.96599 | 5.17 | 5.2184 | 5.2708 | 5.2975 | 5.2927 | N | 6 | 2.4613 | -
Hamley Bridge 11kV | Y | 2.4649 | 2.2677 | 2018-02-07 | 1.504 | 1.486 | 2017-06-04 | 0 | 3 | 3 | 0 | 3 | 0.92 | 2.8047 | 2.8532 | 2.8482 | 2.8624 | 2.858 | N | 5 | 0.75098 | -
Alma 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.96565 | 0.086713 | 0.086534 | 0.086357 | 0.086179 | 0.086002 | N | 6 | 0.0016 | -
SOUTH EAST
MOUNT GAMBIER 33kV | Y | 20.7629 | 20.2371 | 2018-01-18 |  |  |  |  | 66.1 | 63.3 | 32.5 | 50 | 0.97468 | 21.8206 | 25.2435 | 25.3832 | 25.5625 | 25.7444 |  |  | 5.9063
Mount Gambier 11kV | Y | 13.8805 | 13.8652 | 2018-01-28 | 13.391 | 13.306 | 2017-07-03 | 7.8577 | 20 | 25.4441 | 15 | 6.2494 | 0.9989 | 14.1511 | 14.1151 | 14.0215 | 14.1112 | 14.2048 | N | 7 | 5.4486 | -
Tarpeena 11kV | N | - | - | - | - | - | - | 0 | 10 | 9.5 | 5 | 10 | 0.97468 | 4.8107 | 4.8789 | 4.9482 | 5.0184 | 5.0895 | N | 7 | 0.23015 | -
PENOLA WEST 33kV | Y | 7.1914 | 6.7679 | 2018-01-27 |  |  |  |  | 50 | 50 | 25 | 50 | 0.94111 | 9.2802 | 9.3712 | 9.398 | 9.4114 | 9.4254 |  |  | 1.5407
Penola 11kV | Y | 2.8403 | 2.72 | 2018-01-28 | 2.273 | 2.227 | 2017-06-07 | 1.0868 | 3 | 3.9 | 2.25 | 3 | 0.95763 | 2.9047 | 2.8709 | 2.8243 | 2.8163 | 2.8093 | N | 7 | 1.1213 | -
Coonawarra 11kV | Y | 4.3469 | 3.9151 | 2018-01-26 | 1.909 | 1.76 | 2017-06-21 | 0.76294 | 10 | 13.4522 | 7.2 | 5.0195 | 0.90067 | 4.3888 | 4.4543 | 4.4773 | 4.488 | 4.4986 | N | 7 | 0.41274 | -
Nangwarry 11kV | Y | 1.0302 | 0.984 | 2017-12-13 | 1.013 | 0.865 | 2017-08-28 | 0 | 3 | 3.9 | 0 | 3 | 0.95517 | 1.052 | 1.0675 | 1.0777 | 1.0922 | 1.1069 | N | 7 | 0.22754 | -
BLANCHE 33kV | Y | 37.9518 | 36.0594 | 2018-01-28 |  |  |  |  | 110 | 126.3 | 61.5 | 110 | 0.95014 | 38.232 | 38.1689 | 38.0466 | 38.0518 | 38.0679 |  |  | 8.7032
Mount Gambier West 11kV | Y | 16.3379 | 16.0153 | 2018-01-19 | 16.02 | 15.971 | 2017-07-03 | 9.9933 | 20 | 25.636 | 15 | 6.2966 | 0.98026 | 16.3596 | 16.3008 | 16.2538 | 16.2893 | 16.3302 | N | 9 | 3.7579 | -
Mount Gambier North 11kV | Y | 10.0089 | 9.6086 | 2017-11-29 | 7.758 | 7.504 | 2017-06-19 | 6.8418 | 12.5 | 17 | 0 | 12.5 | 0.96 | 10.5868 | 10.5348 | 10.4371 | 10.4424 | 10.451 | N | 7 | 2.5792 | -
Tantanoola 11kV | Y | 0.52879 | 0.504 | 2017-11-27 | 0.55 | 0.525 | 2017-07-27 | 0 | 1 | 1.3 | 0 | 1 | 0.95312 | 0.51409 | 0.51171 | 0.50295 | 0.50189 | 0.50089 | N | 7 | 0.20812 | -
Glencoe 11kV | Y | 1.2049 | 1.084 | 2018-01-28 | 0.675 | 0.672 | 2017-07-01 | 0 | 1.5 | 1.95 | 0 | 1.5 | 0.89968 | 1.1794 | 1.1794 | 1.1692 | 1.1687 | 1.1684 | N | 7 | 0.48423 | -
Kongorong 11kV | Y | 0.84211 | 0.799 | 2018-01-03 | 0.53 | 0.526 | 2017-06-03 | 1.13 | 1 | 1.3 | 0 | 1 | 0.9488 | 0.95148 | 0.94511 | 0.92555 | 0.9234 | 0.92135 | N | 7 | 0.21123 | -
Mount Schank 11kV | Y | 2.8838 | 2.53 | 2018-02-01 | 0.952 | 0.841 | 2017-08-31 | 0.17448 | 3 | 3.9 | 3 | 3 | 0.87731 | 2.9235 | 2.9584 | 2.9855 | 2.9919 | 2.9987 | N | 7 | 0.12556 | -
Allendale East 11kV | Y | 4.3611 | 3.9686 | 2018-01-28 | 3.13 | 2.88 | 2017-06-26 | 0 | 5 | 6.8 | 3.7 | 5 | 0.91 | 4.2927 | 4.2597 | 4.2315 | 4.214 | 4.1981 | N | 7 | 1.1144 | -
KEITH 33kV | Y | 22.9064 | 21.1658 | 2018-01-19 |  |  |  |  | 51 | 58.9 | 37 | 51 | 0.92401 | 24.3745 | 24.6603 | 24.7594 | 24.8819 | 25.0057 |  |  | 5.57
WIRREGA REG 33kV | Y | 10.8811 | 10.1341 | 2018-01-28 | 7.32 | 7.3064 | 2017-06-07 | 0 | 20 | 25 | 0 | 20 | 0.99328 | 10.7901 | 10.9261 | 10.954 | 11.0291 | 11.1041 | N | 7 | - | -
Bordertown 11kV | Y | 9.9527 | 9.5674 | 2018-01-28 | 7.113 | 7.055 | 2017-06-07 | 4 | 10 | 13.4 | 11.2^ | 5 | 0.96129 | 10.7901 | 10.9261 | 10.954 | 11.0291 | 11.1041 | N | 7 | 3.2764 | -
Desert Camp 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.92401 | 0.064241 | 0.064495 | 0.06475 | 0.065006 | 0.065263 | N | 7 | 0.02312 | -
Padthaway 11kV | Y | 3.3971 | 3.2889 | 2018-02-07 | 1.624 | 1.603 | 2017-08-23 | 0 | 10 | 13.8 | 7.4 | 5.8 | 0.96815 | 3.5048 | 3.5385 | 3.5285 | 3.5342 | 3.5396 | N | 9 | 0.53013 | -
Keith 11kV | Y | 5.9065 | 5.2444 | 2018-01-19 | 3.054 | 3.007 | 2017-06-08 | 0 | 12.5 | 16.5904 | 8.8 | 4.9971 | 0.8879 | 5.906 | 5.9016 | 5.8846 | 5.8831 | 5.8833 | N | 3 | 1.2528 | -
[14 empty] | 1.2848 | 1.2899 | 1.295 | 1.3001 | 1.3053
Tintinara 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0.75 | 1 | 0.92401 | 1.285 | 1.291 | 1.305 | 1.311 | 1.315 | Y | 7 | 0.37734 | -
Kumorna 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.92401 | 0.64241 | 0.64495 | 0.6475 | 0.65006 | 0.65263 | N | 7 | 0 | -
^Up to 4MW of third party generation installed at Bordertown Substation with a staged network support contract commencing in 2013 | bar: MVA to Date
KINCRAIG 33kV | Y | 19.9345 | 19.212 | 2018-01-18 |  |  |  |  | 50 | 51.6 | 30.5 | 50 | 0.96376 | 20.6244 | 20.6442 | 20.4828 | 20.4688 | 20.3525 |  |  | 7.2242
Naracoorte 11kV | Y | 11.1489 | 10.4627 | 2018-01-28 | 10.609 | 10.218 | 2017-06-07 | 0.77912 | 25 | 27.8 | 14.8 | 10.2 | 0.93845 | 11.3875 | 11.3095 | 11.1688 | 11.1374 | 11.052 | N | 7 | 4.453 | -
Naracoorte East 11kV | Y | 5.2851 | 4.7633 | 2018-01-05 | 0.64 | 0.618 | 2017-08-08 | 4.8214 | 12.5 | 17.2 | 0 | 12.5 | 0.90127 | 5.4942 | 5.5993 | 5.654 | 5.67 | 5.6563 | N | 9 | 0.43525 | -
Lucindale 11kV | Y | 1.2536 | 1.224 | 2018-01-28 | 0.9 | 0.89 | 2017-06-03 | 0 | 3 | 3.9 | 2.25 | 3 | 0.97636 | 1.3267 | 1.326 | 1.3011 | 1.2999 | 1.2919 | N | 5 | 0.44172 | -
KINGSTON PT REG 33kV | N | - | - | - | - | - | - | 0 | 11.4 | 14.861 | 0 | 11.4 |  | 3.2857 | 3.2557 | 3.1771 | 3.1675 | 3.1421 | N | 7 | - | -
Kingston SE 11kV | Y | 3.0627 | 3.062 | 2018-01-28 | 2.87 | 2.766 | 2017-08-05 | 0 | 3 | 3.9 | 2.25 | 3 | 0.99978 | 3.2857 | 3.2557 | 3.1771 | 3.1675 | 3.1421 | N | 7 | 1.7883 | -
Inverness 11kV | Y | 0.26822 | 0.23 | 2018-03-08 | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.85749 | 0.36062 | 0.36887 | 0.37331 | 0.37418 | 0.37306 | N | 7 | 0 | -
SNUGGERY RURAL 33kV | Y | 13.4844 | 13.0743 | 2018-01-18 |  |  |  |  | 25 | 28.8 | 28.8 | 25 | 0.96959 | 14.9731 | 14.988 | 14.8317 | 14.8913 | 14.9526 |  |  | 6.5057
Millicent 11kV | Y | 5.713 | 5.4648 | 2018-01-28 | 6.225 | 6.155 | 2017-07-01 | 0 | 10 | 13.2 | 7.1 | 5.0258 | 0.95656 | 5.9971 | 5.9467 | 5.8277 | 5.8411 | 5.8546 | N | 6 | 3.2111 | -
South End 11kV | Y | 0.4453 | 0.432 | 2018-01-01 | 0.4022 | 0.398 | 2017-06-04 | 0 | 0.6 | 0.78 | 0.45 | 0.6 | 0.97014 | 0.54361 | 0.54272 | 0.53043 | 0.53227 | 0.52757 | N | 6 | 0.40771 | -
Hatherleigh 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96959 | 0.065398 | 0.065196 | 0.064994 | 0.064793 | 0.064592 | N | 6 | 0.03318 | -
HATHERLEIGH REG 33kV | N | - | - | - | - | - | - | 0 | 10 | 12.5 | 0 | 10 |  | 5.266 | 5.2612 | 5.1885 | 5.202 | 5.2197 | N | 6 | - | -
Beachport 11kV | Y | 1.1346 | 1.106 | 2018-01-18 | 0.875 | 0.872 | 2017-06-03 | 0 | 2.5 | 2.7 | 0 | 2.5 | 0.97482 | 1.2234 | 1.2086 | 1.178 | 1.1786 | 1.1803 | N | 6 | 0.67599 | -
Robe 7.6kV | Y | 2.7154 | 2.683 | 2018-01-18 | 2.25 | 2.249 | 2017-06-10 | 0 | 5 | 6.5 | 3.75 | 5 | 0.98808 | 4.0426 | 4.0526 | 4.0105 | 4.0234 | 4.0394 | N | 2 | 1.0812 | -
Mount Burr 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96959 | 0.368 | 0.374 | 0.381 | 0.388 | 0.395 | Y | 6 | 0.17868 | -
Kalangadoo West 11kV | Y | 0.84177 | 0.783 | 2018-01-28 | 0.6977 | 0.659 | 2017-08-13 | 0 | 1 | 1.3 | 0.75 | 1 | 0.93019 | 0.85436 | 0.85285 | 0.836 | 0.83913 | 0.84288 | N | 4 | 0.10327 | -
Kalangadoo 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.96959 | 0.56056 | 0.55882 | 0.55709 | 0.55536 | 0.55365 | N | 6 | 0.19487 | -
RIVERLAND
BERRI / MONASH 66kV | Y | 89.4757 | 87.5526 | 2018-01-28 |  |  |  |  | 160 | 190 | 140 | 75 | 0.97851 | 92.1087 | 91.8092 | 92.3713 | 92.3374 | 92.3545 |  |  | 32.4306
Berri 11kV | Y | 11.6301 | 10.9852 | 2018-02-08 | 7.189 | 7.011 | 2017-06-01 | 3.5106 | 20 | 28 | 15 | 20 | 0.94455 | 11.7985 | 11.6037 | 11.5845 | 11.5462 | 11.5148 | N | 9 | 5.3293 | -
Loxton 11kV | Y | 12.5318 | 12.4964 | 2018-01-28 | 6.851 | 6.851 | 2017-06-29 | 0.35474 | 18.8 | 19.9052 | 14.5746 | 9.406 | 0.99718 | 12.1892 | 12.0527 | 12.1403 | 12.1163 | 12.0991 | N | 8 | 3.3412 | -
Pyap 11kV | Y | 8.6763 | 8.5544 | 2018-01-28 | 4.511 | 4.503 | 2017-06-04 | 0.97881 | 12.5 | 15.1699 | 7.5 | 5.9615 | 0.98596 | 8.6533 | 8.5996 | 8.5922 | 8.5929 | 8.5961 | N | 5 | 3.5817 | -
Lyrup 11kV | Y | 3.9462 | 3.6617 | 2018-01-21 | 1.936 | 1.781 | 2017-06-24 | 1.214 | 5 | 6.5 | 3.75 | 3.8 | 0.92791 | 4.1692 | 4.3561 | 4.6006 | 4.8025 | 5.0051 | N | 20 | 1.1515 | -
Paringa 33kV | Y | 13.8158 | 13.3 | 2018-01-20 | 6.04 | 5.9 | 2017-08-14 | 14.8 | 32 | 36.575 | 0 | 32 | 0.96266 | 13.6678 | 13.6884 | 13.9282 | 13.9546 | 13.987 | N | 9 | 2.3577 | -
Paringa 11kV | Y | 2.675 | 2.5816 | 2018-01-28 | 1.62 | 1.6 | 2017-06-02 | 3.88 | 2.5 | 3.25 | 0 | 2.5 | 0.9651 | 2.5763 | 2.5196 | 2.5222 | 2.5142 | 2.5083 | N | 5 | 1.3516 | -
Renmark 11kV | Y | 18.708 | 18.6103 | 2018-01-19 | 11.61 | 11.586 | 2017-06-07 | 0 | 22.5 | 28.5 | 21.2 | 22.5 | 0.99478 | 19.0807 | 18.6998 | 18.7265 | 18.6752 | 18.6377 | N | 6 | 8.7714 | -
Glossop 11kV | Y | 9.1366 | 8.7216 | 2018-02-23 | 6.069 | 5.99 | 2017-06-21 | 3.4713 | 12.5 | 15.3526 | 7.5 | 6.2823 | 0.95457 | 9.8 | 10.5133 | 10.5627 | 10.518 | 10.4787 | N | 6 | 2.6106 | -
Loveday 11kV | Y | 12.3685 | 12.3663 | 2018-01-28 | 6.938 | 6.916 | 2017-06-07 | 0.67305 | 15 | 20.3622 | 14.6267 | 8.5334 | 0.99983 | 11.9446 | 11.701 | 11.6893 | 11.6351 | 11.5894 | N | 6 | 5.0069 | -
Woolpunda 11kV | Y | 6.2405 | 5.7812 | 2018-01-06 | 3.806 | 2.958 | 2017-08-17 | 0.60653 | 15 | 18.8 | 10.6 | 15 | 0.9264 | 6.3163 | 6.3455 | 6.4369 | 6.4446 | 6.4538 | N | 9 | 0.28042 | -
NORTH WEST BEND 66kV | Y | 29.0145 | 27.2235 | 2018-01-21 |  |  |  |  | 65 | 73.6 | 55.6 | 60 | 0.93827 | 29.5399 | 29.7328 | 29.8283 | 29.8071 | 29.7898 |  |  | 8.7264
Cadell 11kV | N | - | - | - | - | - | - | 0 | 2 | 2.6 | 1.5 | 2 | 0.93827 | 2.546 | 2.5489 | 2.5519 | 2.5549 | 2.5578 | N | 5 | 0.70947 | -
Qualco 11kV | N | - | - | - | - | - | - | 2.0071 | 2.5 | 3.25 | 0 | 2.1 | 0.93827 | 2.9533 | 2.9568 | 2.9602 | 2.9637 | 2.9671 | N | 5 | 0.14081 | -
Ramco 11kV | Y | 6.4041 | 5.943 | 2018-01-21 | 2.663 | 2.431 | 2017-06-24 | 3.406 | 7 | 8.4 | 4.8 | 7 | 0.928 | 6.5507 | 6.6037 | 6.6181 | 6.6103 | 6.6028 | N | 5 | 2.5706 | -
Waikerie 11kV | Y | 7.8372 | 7.6972 | 2018-01-28 | 5.2 | 5.18 | 2017-07-20 | 1.4526 | 10 | 12.0467 | 6.7 | 9.1263 | 0.98214 | 7.6134 | 7.5088 | 7.4383 | 7.3847 | 7.3346 | N | 6 | 3.1217 | -
Morgan 11kV | N | - | - | - | - | - | - | 0 | 1 | 1.3 | 0 | 1 | 0.93827 | 1.1202 | 1.1215 | 1.1228 | 1.1241 | 1.1254 | N | 6 | 0.49948 | -
Cordola 11kV | N | - | - | - | - | - | - | 0 | 2 | 2.6 | 1.5 | 2 | 0.93827 | 2.1386 | 2.1411 | 2.1436 | 2.1461 | 2.1486 | N | 6 | 0.34852 | -
Roonka 11kV | Y | 3.0949 | 2.8085 | 2018-01-27 | 1.441 | 1.368 | 2017-06-11 | 3.75 | 6.25 | 8.1 | 0 | 6.25 | 0.90746 | 3.2025 | 3.2024 | 3.1864 | 3.1787 | 3.1716 | N | 6 | 0.9736 | -
Portee 11kV | Y | 0.60968 | 0.57983 | 2018-01-05 | 0.366 | 0.337 | 2017-08-13 | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.95104 | 0.626 | 0.631 | 0.637 | 0.643 | 0.649 | N | 6 | 0.01724 | -
Swan Reach 11kV | Y | 1.3412 | 1.262 | 2017-12-27 | 1.058 | 0.986 | 2017-07-26 | 0 | 3 | 3.9 | 0 | 3 | 0.94096 | 1.371 | 1.3657 | 1.3492 | 1.3478 | 1.3467 | N | 4 | 0.34313 | -
Swan Reach 33kV | Y | 2.105 | 1.931 | 2018-01-28 | 1.003 | 0.915 | 2017-07-26 | 0 | 7.5 | 10.69 | 0 | 5.8 | 0.93827 | 2.5728 | 2.5758 | 2.5788 | 2.5818 | 2.5848 | N | 4 | 0.34504 | -
UPPER NORTH
DAVENPORT WEST 33kV | Y | 29.0474 | 28.9099 | 2018-02-08 |  |  |  |  | 120 | 120 | 60 | 120 | 0.99527 | 39.7698 | 39.6128 | 39.5815 | 39.406 | 39.2456 |  |  | 11.405
Port Augusta 11kV | Y | 12.6616 | 12.614 | 2018-02-08 | 9.42 | 9.418 | 2017-07-11 | 8.9133 | 20 | 28.4 | 15 | 7.6 | 0.99624 | 13.8924 | 13.7736 | 13.6644 | 13.5691 | 13.4829 | N | 9 | 4.0416 | -
Port Augusta West TF1 11kV | Y | 7.8891 | 7.56 | 2018-02-08 | 4.86 | 4.855 | 2017-08-24 | 7.5637 | 12.5 | 14.8 | 0 | 1.4 | 0.95828 | 5.7734 | 5.7364 | 5.7142 | 5.6824 | 5.6545 | N | 7 | 1.7905 | -
Port Augusta West TF2 11kV | Y | 1.8153 | 1.7729 | 2018-02-08 | 1.239 | 1.236 | 2017-08-04 | 3.4922 | 12.5 | 14.8 | 0 | 1.4 | 0.97665 | 1.9324 | 1.7999 | 1.7173 | 1.6706 | 1.6274 | N | 7 | 1.8813 | -
Stirling North TF1 11kV | Y | 2.9284 | 2.577 | 2018-01-19 | 1.1327 | 1.128 | 2017-08-04 | 1.7587 | 2.5 | 3.25 | 0 | 2.5 | 0.88 | 1.7661 | 1.6955 | 1.671 | 1.6391 | 1.6098 | N | 6 | 1.0933 | -
Stirling North TF2 11kV | Y | 1.7301 | 1.697 | 2018-02-08 | 1.24 | 1.237 | 2017-08-04 | 1.7087 | 3 | 3.9 | 0 | 3 | 0.98085 | 1.7004 | 1.6887 | 1.6747 | 1.6633 | 1.6528 | N | 6 | 0.97937 | -
Quorn 11kV | Y | 1.8437 | 1.808 | 2018-01-21 | 1.776 | 1.766 | 2017-08-07 | 1.5 | 2.5 | 2.7 | 0 | 2.5 | 0.98064 | 1.9287 | 1.9107 | 1.8785 | 1.8643 | 1.8375 | N | 6 | 1.0752 | -
BAROOTA 33kV | Y | 7.6693 | 7.6639 | 2018-02-08 |  |  |  |  | 10 | 11.8 | 0 | 10 | 0.9993 | 8.2744 | 8.2867 | 8.2126 | 8.2266 | 8.2414 |  |  | 4.5617
Baroota 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0 | 0.9993 | 0.29222 | 0.29123 | 0.29024 | 0.28926 | 0.28828 | N | 6 | 0.05955 | -
Bungama Napperby 11kV | Y | 1.0917 | 1.0153 | 2018-01-19 | 0.753 | 0.692 | 2017-06-11 | 0 | 1 | 1.3 | 0.75 | 1 | 0.93 | 1.2195 | 1.1686 | 1.1289 | 1.1132 | 1.0984 | N | 7 | 0.79978 | -
Telowie 11kV | Y | 0.56652 | 0.559 | 2018-02-08 | 0.439 | 0.439 | 2017-08-04 | 0.61296 | 1 | 1 | 0 | 1 | 0.98673 | 0.61229 | 0.61663 | 0.61102 | 0.60331 | 0.59603 | N | 7 | 0.47925 | -
Port Germein 11kV | Y | - | - | - | - | - | - | 0.948 | 1 | 1.3 | 0 | 1 | 0.99322 | 0.90714 | 0.89728 | 0.86516 | 0.86604 | 0.86682 | N | 7 | 0.66128 | -
MURRAYTOWN REG 33kV | Y | - | - | - | - | - | - | 0 | 10 | 12.5 | 0 | 10 |  | 3.8395 | 3.7962 | 3.7513 | 3.7331 | 3.7156 | N | 6 | - | -
Wongyarra 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.9993 | 0.096421 | 0.096095 | 0.09577 | 0.095446 | 0.095123 | N | 7 | 0.01286 | -
Wirrabara Forest 11kV | Y | 0.44202 | 0.41108 | 2017-11-22 | 0.457 | 0.42 | 2017-07-22 | 0 | 1 | 1.3 | 0 | 1 | 0.93 | 0.55246 | 0.55223 | 0.54563 | 0.54544 | 0.54522 | N | 6 | 0.10966 | -
Wirrabara South 11kV | N | - | - | - | - | - | - | 0 | 0.1 | 0.13 | 0 | 0.1 | 0.9993 | 0.048211 | 0.048048 | 0.047885 | 0.047723 | 0.047562 | N | 7 | 0.00304 | -
Fullerville 11kV | N | - | - | - | - | - | - | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.9993 | 0.029222 | 0.029123 | 0.029024 | 0.028926 | 0.028828 | N | 7 | 0 | -
Booleroo Centre 11kV | Y | 0.55443 | 0.51562 | 2018-01-19 | 0.547 | 0.503 | 2017-08-02 | 0 | 1 | 1.3 | 0 | 1 | 0.93 | 0.5735 | 0.56402 | 0.56036 | 0.55578 | 0.55146 | N | 1 | 0.28929 | -
Orroroo 11kV | N | - | - | - | - | - | - | 0 | 2 | 2.6 | 1.5 | 2 | 0.9993 | 1.4611 | 1.4561 | 1.4512 | 1.4463 | 1.4414 | N | 7 | 0.79786 | -
Melrose 11kV | N | - | - | - | - | - | - | 0 | 0.5 | 0.65 | 0 | 0.5 | 0.9993 | 0.3117 | 0.31064 | 0.30959 | 0.30854 | 0.3075 | N | 7 | 0.19885 | -
Wilmington 11kV | Y | 0.75733 | 0.749 | 2018-01-27 | 0.584 | 0.582 | 2017-08-04 | 0 | 2 | 2 | 0 | 2 | 0.989 | 0.76686 | 0.73986 | 0.71177 | 0.70495 | 0.69852 | N | 7 | 0.54084 | -
LEIGH CREEK SOUTH 33kV | Y | 1.0429 | 1.0373 | 2017-12-18 |  |  |  |  | 10 | 10 | 5 | 10 | 0.99467 | 1.1338 | 1.1172 | 1.0925 | 1.0863 | 1.0805 |  |  | 0.35375
Leigh Creek South 11kV | N | - | - | - | - | - | - | 0 | 5 | 6.5 | 3.75 | 5 | 0.99 | 1.1338 | 1.1172 | 1.0925 | 1.0863 | 1.0805 | N | 7 | 0.10871 | -
Copley-Nepabunna 33kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.4 | 0 | 0.3 |  | - | - | - | - | - |  | 7 | - | -
BUNGAMA / PORT PIRIE 33kV | Y | 66.7693 | 64.5225 | 2018-01-19 |  |  |  |  | 180 | 192 | 140 | 180 | 0.96635 | 73.5759 | 73.6794 | 73.7828 | 73.8863 | 73.8863 |  |  | 23.4278
HUGHES GAP REG 33kV | Y | 8.1197 | 7.823 | 2018-02-08 | 7.51 | 7.36 | 2017-08-02 | 0 | 20 | 13.7 | 0 | 13.7 | 0.95959 | 6.908 | 6.8538 | 6.7936 | 6.7856 | 6.7757 | N | 1 | - | -
Booyoolie 11kV | N | - | - | - | - | - | - | 0 | 0.15 | 0.195 | 0 | 0.15 | 0.96635 | 0.020484 | 0.020524 | 0.020565 | 0.020605 | 0.020646 | N | 2 | 0.00304 | -
Gladstone 11kV | N | - | - | - | - | - | - | 0.60719 | 4 | 4.8 | 2.56 | 4 | 0.96635 | 2.5604 | 2.5655 | 2.5706 | 2.5756 | 2.5807 | N | 2 | 1.2912 | -
GLADSTONE REG 33kV | N | - | - | - | - | - | - | 0 | 10 | 12.5 | 0 | 10 |  | 6.8875 | 6.8332 | 6.773 | 6.765 | 6.755 | N | 2 | - | -
Caltowie 11kV | Y | 0.10479 | 0.097454 | 2018-01-19 | 0.101 | 0.093 | 2017-06-19 | 0 | 0.2 | 0.26 | 0 | 0.2 | 0.93 | 0.088029 | 0.083715 | 0.080634 | 0.079378 | 0.078077 | N | 2 | 0.10094 | -
Yongala 11kV | N | - | - | - | - | - | - | 0 | 0.3 | 0.39 | 0 | 0.3 | 0.96635 | 0.10348 | 0.10348 | 0.10348 | 0.10348 | 0.10348 | N | 2 | 0.06194 | -
Peterborough 11kV | Y | 1.8288 | 1.813 | 2018-01-21 | 2.012 | 1.992 | 2017-06-01 | 0 | 5 | 6.2 | 3.5 | 5 | 0.99134 | 1.8256 | 1.7705 | 1.7084 | 1.6965 | 1.6827 | N | 6 | 1.1154 | -
Jamestown 11kV | Y | 2.2757 | 2.167 | 2018-02-08 | 2.184 | 2.158 | 2017-06-06 | 0 | 3 | 3.9 | 2.25 | 3 | 0.952 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | N | 6 | 1.4571 | -
Crystal Brook 11kV | Y | 1.999 | 1.938 | 2018-01-28 | 1.532 | 1.514 | 2017-08-02 | 2.5794 | 2 | 2.6 | 1.5 | 2 | 0.96949 | 1.9875 | 1.9342 | 1.8911 | 1.8733 | 1.8536 | N | 2 | 1.0217 | -
Port Broughton 11kV | Y | 2.8712 | 2.6415 | 2018-01-19 | 2.314 | 2.12 | 2017-06-11 | 0 | 5 | 5.4 | 3 | 5 | 0.92 | 3.212 | 3.0937 | 3.0101 | 2.9765 | 2.9408 | N | 3 | 1.8706 | -
Port Pirie South 11kV | Y | 20.6958 | 20.0869 | 2018-02-08 | 14.189 | 14.056 | 2017-08-28 | 0.948 | 37.5 | 40.5097 | 27.7358 | 10.8026 | 0.97058 | 23.3538 | 23.0563 | 22.8042 | 22.7881 | 22.7438 | N | 7 | 9.9688 | -
NEUROODLA 33kV | Y | 0.88676 | 0.8829 | 2018-01-21 |  |  |  |  | 10 | 10 | 0 | 10 | 0.99565 | 0.93853 | 0.94085 | 0.93353 | 0.93259 | 0.9317 |  |  | 0.32973
Hawker 11kV | Y | 0.85001 | 0.85 | 2018-01-21 | 0.75 | 0.742 | 2017-08-20 | 0 | 1 | 1.3 | 0.75 | 1 | 0.99999 | 0.90945 | 0.91156 | 0.90422 | 0.9033 | 0.90243 | N | 2 | 0.32973 | -
Note on A276: Author: override with 2017 forecast based on measured logger's peak